## Cover & Index
220 kV TRANSMISSION LINE PROTECTION RELAY TEST PROTOCOL
220kV A – B Line ¦ Distance Protection (Siemens 7SA612 & SEL-421-5) ¦ Backup OC/EF ¦ CT: 1200/1 ¦ VT: 220kV/110V ¦ Line: 68.50 km
Standards: IEC 60255 Series ¦ IEC 60834-1 ¦ IEC 61869 ¦ IEC 61850 ¦ ANSI/IEEE C37.90 ¦ NTDC/WAPDA Guidelines ¦ Saudi Aramco SAES-P-111 ¦ SEC Standards
PROJECT INFORMATION
Project Name / Contract No.
Line Designation |  | 220kV ABC
From Substation |  | A 220kV Grid Station
To Substation |  | B 220kV Grid Station
Voltage Level (kV) |  | 220 kV
Line Length (km) |  | 68.50 km
CT Ratio |  | 1200 / 1 A
VT Ratio |  | 220 kV / 110 V (Secondary 110 V)
Conductor Type |  | Twin Rail (Zebra ACSR)
Positive-Seq. Impedance Z1 |  | R1 = 0.031099 Ω/km ¦ X1 = 0.2852 Ω/km ¦ Z1_total = 19.65 Ω (pri)
Zero-Seq. Impedance Z0 |  | R0 = 0.123 Ω/km ¦ X0 = 0.800 Ω/km ¦ Z0_total = 55.44 Ω (pri)
kZE (Zero-Seq. Compensation) |  | 0.606 [(Z0−Z1)/(3×Z1)]
Line Angle (°) |  | 83.78°
Primary Relay 1 |  | Siemens 7SA6121-5BB92-6PB4+LOS ¦ PUTT (FCT85)
Primary Relay 2 |  | SEL-421-5 ¦ POTT Scheme
Backup Relay |  | Siemens 7SJ8021-5EB90-1FA0 ¦ OC/EF Backup
Client / Owner |  | NTDC (National Transmission & Despatch Company)
Contractor |  | Siemens Pakistan Engineering Co. Ltd.
Test Date
Test Engineer
Witness / Client
Report No.
Ambient Temperature (°C)
DC Supply Voltage (V)
TEST EQUIPMENT USED
Equipment |  | Make / Model | Serial No. | Cal. Cert No. | Cal. Due Date | Remarks
6-Phase Secondary Injection Test Set (OMICRON CMC 356 / Doble F6150)
Multimeter / True RMS Phase Angle Meter
Insulation Resistance Tester 500 VDC (Megger)
Laptop + DIGSI 4/5 Software (7SA612) + AcSELerator Quickset (SEL-421)
GPS / IRIG-B Time Synchronisation Source
CT & VT Test Set (Ratio & Polarity)
Earth Resistance Tester (4-wire Kelvin)
Oscilloscope (optional for waveform capture)
TEST SHEET INDEX
Sheet | Test Description |  |  | Relay | ANSI Ref | IEC Reference | Status
Sh.2 | Pre-Test Checks & Insulation Resistance |  |  | Both | – | IEC 60255-27 | PENDING
Sh.3 | Relay Settings Record – Distance Zones & Features (7SA612 & SEL-421) |  |  | Both | 21 | IEC 60255-121 | PENDING
Sh.4 | Zone 1 Reach Accuracy & Trip Timing |  |  | Both | 21-Z1 | IEC 60255-121 | PENDING
Sh.5 | Zone 1B SOTF Extension (7SA612) / Zone 2 POTT (SEL-421) |  |  | Both | 21-Z1B/Z2 | IEC 60255-121 | PENDING
Sh.6 | Zone 2 Reach Accuracy & Timing (7SA612) / Zone 4 (SEL-421) |  |  | Both | 21-Z2/Z4 | IEC 60255-121 | PENDING
Sh.7 | Zone 3 / Zone 5 Non-Directional Reach & Timing |  |  | 7SA612 | 21-Z3/Z5 | IEC 60255-121 | PENDING
Sh.8 | Directional Element Test (Forward / Reverse) |  |  | Both | 21D / 32 | IEC 60255-121 | PENDING
Sh.9 | Power Swing Detection & Blocking (PSB/OOS) |  |  | Both | 68 / 78 | IEC 60255-121 | PENDING
Sh.10 | Load Encroachment / Load Blinder Test |  |  | Both | 21LE | IEC 60255-121 | PENDING
Sh.11 | VT Fuse Failure / Loss of Potential (VTFF / LOP) |  |  | Both | 60FL | IEC 60255-121 | PENDING
Sh.12 | Teleprotection – PUTT (FCT85) / POTT (SEL-421) |  |  | Both | 85 | IEC 60834-1 | PENDING
Sh.13 | Switch-On-To-Fault (SOTF) |  |  | Both | 50/SOTF | IEC 60255-151 | PENDING
Sh.14 | Backup OC/EF – Siemens 7SJ8021 (51/51N) |  |  | Backup | 51/51N | IEC 60255-151 | PENDING
Sh.15 | Fault Locator Test & Verification |  |  | Both | FL | IEC 60255-121 | PENDING
Sh.16 | CT & VT Checks – Polarity, Ratio, Knee Point |  |  | Both | – | IEC 61869 | PENDING
Sh.17 | Trip Circuit Supervision & End-to-End Trip Tests |  |  | Both | 74 | IEC 61850 | PENDING
Sh.18 | Test Summary, Defects Log & Overall Result |  |  | Both | – | – | PENDING
APPLICABLE STANDARDS: IEC 60255 (Protective Relays) ¦ IEC 60834-1 (Teleprotection) ¦ IEC 61869 (CTs & VTs) ¦ IEC 61850 (Communication/SCADA) ¦ ANSI/IEEE C37.90 ¦ NTDC/WAPDA Protection Testing Guidelines ¦ Saudi Aramco SAES-P-111 (HV Protection) ¦ SEC (Saudi Electricity Co.) – Distribution & Transmission Protection Standards
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:
📐 KEY LINE PARAMETERS & VERIFICATION FORMULAS — 220kV A–Mardan
Z1 Primary (Ω) |  | Z1_pri = √(R1²+X1²) × L = √(0.0311²+0.2852²) × 68.5 = 0.2869 × 68.5 = 19.65 Ω
Z0 Primary (Ω) |  | Z0_pri = √(R0²+X0²) × L = √(0.123²+0.800²) × 68.5 = 0.809 × 68.5 = 55.42 Ω
kZE Factor |  | kZE = (Z0−Z1) / (3×Z1) = (55.42−19.65) / (3×19.65) = 35.77/58.95 = 0.606
Z_secondary (7SA612) |  | Z_sec = Z_pri × (CT/VT) = Z_pri × (1/1200)/(110/220000) = Z_pri × 0.600
Z_secondary (SEL-421) |  | Z_sec = Z_pri × (CT/VT) = Z_pri × (1/1200)/(110/2,000,000) × 1000 = Z_pri × 0.0600 × VT_ratio_correction
VT Ratio (7SA612) |  | VT ratio = 220,000 V / 110 V = 2,000 ¦ CT ratio = 1200/1 A ¦ Conversion: Z_pri = Z_sec / 0.600
CT Secondary In |  | Rated secondary current In = 1 A ¦ Max primary load = 1200 A ¦ Rated load Z = 220²/(√3×1200×10⁻³) = 105.1 Ω primary
IR Acceptance |  | R_insulation ≥ 100 MΩ at 500 VDC per IEC 60255-27 Table 7
DC Supply Tolerance |  | V_dc = V_rated ± 10% (e.g., 220VDC → acceptable range: 198 V – 242 V)
Earth Bond Check |  | R_earth < 1 Ω (measured by 4-wire Kelvin / earth resistance tester)
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 |  | Measuring relays – Distance protection relays: performance requirements, test procedures, accuracy classes
IEC 60255-151:2009 |  | Measuring relays – Functional requirements for overcurrent protection relays
IEC 60255-27:2013 |  | Measuring relays and protection equipment – General requirements (IR, EMC, withstand)
IEC 60834-1:1999 |  | Teleprotection equipment for EHV/HV power systems – Performance and testing
IEC 61869-2:2012 |  | Instrument transformers – Current transformers – Additional requirements
IEC 61869-3:2011 |  | Instrument transformers – Inductive voltage transformers – Additional requirements
IEC 61850-5:2013 |  | Communication networks in substations – Function and device models (GOOSE, trip supervision)
ANSI/IEEE C37.90-2005 |  | Relays and relay systems associated with electric power apparatus – General requirements
ANSI/IEEE C37.113-2015 |  | IEEE Guide for Protective Relay Applications to Transmission Lines
NTDC/WAPDA Guidelines |  | National Transmission & Despatch Co. – Protection relay testing & commissioning guidelines (Pakistan)
Saudi Aramco SAES-P-111 |  | Protection of high voltage (≥ 34.5 kV) systems – relay coordination, testing acceptance
SEC T&D Standards |  | Saudi Electricity Company – Transmission & distribution protection standards for EHV lines
BS 3938:1982 |  | Current transformers – British Standard (superseded by IEC 61869-2 but referenced in NTDC specs)

## Pre-Test Checks
PRE-TEST CHECKS & INSULATION RESISTANCE ¦ IEC 60255-27 ¦ 220kV A–B
LINE: 220kV A – B ¦ CT: 1200/1 A ¦ VT: 220kV/110V ¦ Standards: IEC 60255-27 ¦ IEEE C37.90.0 ¦ NTDC/WAPDA Guidelines
PROCEDURE: (1) Complete visual inspection before any injection tests. (2) Perform IR test at 500 VDC – minimum ≥ 100 MΩ required (IEC 60255-27 Table 7). (3) Record ambient temperature – IR is temperature dependent. (4) All CT secondary shorting links must be removed before injection. (5) If any IR reading < 100 MΩ – STOP, locate and rectify the fault before proceeding. FORMULAS: IR acceptance: R_ins ≥ 100 MΩ @ 500 VDC. DC supply: V_dc = V_rated ± 10% (e.g. 220VDC → 198–242V). Earth bond: R < 1 Ω (4-wire Kelvin method).
A. VISUAL & MECHANICAL INSPECTION
S.No | Check Item |  | Requirement |  | Result / Measured | Pass/Fail | Initials | Remarks
1 | Relay panels physically secure – no physical damage or loose fittings |  | No damage
2 | All wiring correct per approved scheme drawings (G76001-EA087) |  | Per drawings
3 | CT 1200/1 connections & polarity verified (P1→S1 facing line) |  | Correct polarity
4 | CT secondary shorting links removed before injection testing |  | Confirmed removed
5 | VT 220kV/110V connections and fuses healthy |  | VT supply OK
6 | Earth connections solid – measured resistance < 1 Ω |  | < 1 Ω measured
7 | DC auxiliary supply measured at relay terminals = rated ± 10% |  | V_dc ± 10%
8 | Trip fuses / MCBs rated correctly per protection schedule |  | Per schedule
9 | Binary input / output wiring verified per scheme drawings |  | Per drawings
10 | Relay firmware version noted and approved for use |  | Version on record
11 | Teleprotection channel (FCT85/POTT COMM) healthy – comms active |  | Comms active
12 | GPS / IRIG-B time sync confirmed – relay time synchronised |  | Sync active
13 | Fault locator VT input connected and healthy |  | VT input OK
14 | Relay self-diagnostics healthy – no fault LEDs on power-up |  | All LEDs green
15 | SOTF logic wiring (CB 52b/52a contacts) verified per scheme |  | Per drawings
16 | Load encroachment VT / CT inputs confirmed healthy |  | Inputs healthy
17 | CB position contacts (52A) wired and verified |  | Verified
18 | All CT/VT secondary burdens within rated CT/VT burden limits |  | Within limits
B. INSULATION RESISTANCE TEST (500 VDC Megger) — IEC 60255-27 Cl. 8.4 ¦ Minimum ≥ 100 MΩ
# | Circuit Under Test |  | Test V (VDC) | Min. (MΩ) | Measured Before (MΩ) | Measured After (MΩ) | Temp (°C) | Pass/Fail | Initials
1 | Phase CT (R-phase) circuit to Earth |  | 500 | ≥ 100
2 | Phase CT (Y-phase) circuit to Earth |  | 500 | ≥ 100
3 | Phase CT (B-phase) circuit to Earth |  | 500 | ≥ 100
4 | Neutral / Earth CT circuit to Earth |  | 500 | ≥ 100
5 | VT phase circuits to Earth |  | 500 | ≥ 100
6 | Trip Circuit to Earth |  | 500 | ≥ 100
7 | Teleprotection FCT85 / POTT circuits to Earth |  | 500 | ≥ 100
8 | DC Auxiliary supply circuit to Earth |  | 500 | ≥ 100
9 | Binary input circuits to Earth |  | 500 | ≥ 100
10 | Relay case / chassis to Earth |  | 500 | ≥ 100
C. TEST EQUIPMENT RECORD
Equipment |  | Make / Model |  | Serial No. | Cal. Cert. No. | Cal. Due Date | Range Used | Remarks
Secondary Injection Test Set (OMICRON CMC 356 / Doble F6150)
Multimeter / Phase Angle Meter (True RMS)
Insulation Resistance Tester 500 VDC
CT Test Set (ratio & polarity)
Earth Resistance Tester (Kelvin 4-wire)
Laptop + Relay Configuration Software
GPS / IRIG-B Time Synchronisation Source
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – PRE-TEST CHECKS
Insulation Resistance |  | R_ins ≥ 100 MΩ @ 500 VDC ¦ Per IEC 60255-27 Table 7 ¦ Temperature correction: R_corrected = R_measured × 1.5^((T_ref−T_meas)/10)
DC Supply Tolerance |  | V_acceptable = V_rated × (1 ± 0.10) → e.g. 220 VDC: 198 V ≤ V ≤ 242 V ¦ Measure at relay terminals (not bus)
Earth Bond Resistance |  | R_earth < 1 Ω (4-wire Kelvin method) ¦ R = V_sense / I_source ¦ Acceptance per IEC 60255-27 Cl. 8.3
CT Burden Check |  | Z_burden(Ω) = V_CT² / S_rated ¦ Must be < CT rated burden ¦ Also: Z_burden = R_lead + R_relay + R_wiring
CT Shorting Requirement |  | I_CT_secondary = I_primary / CT_ratio ¦ Open secondary → V = I × Z_loop → dangerous high voltage! Must short before disconnecting
Phase Rotation Check |  | Verify R-Y-B or A-B-C sequence clockwise using phase rotation meter ¦ Incorrect rotation → relay maloperation
Relay Firmware |  | Firmware version must match approved software revision listed in relay manual and NGC approval letter
📊 STANDARD DEVIATION – INSULATION RESISTANCE MEASUREMENTS
Standard deviation quantifies the spread of repeated timing measurements. A low σ indicates consistent relay operation. Per IEC 60255-121: if σ > 5 ms for instantaneous zones or > 3% of set time for timed zones → investigate relay or test set.
Measurement Set | n (samples) | Mean x̄ (ms) | Std Dev σ (ms) | Variance σ² (ms²) | Min (ms) | Max (ms) | Range (ms) | CoV (%) | Acceptance (IEC 60255-121)
Phase R IR (MΩ) | 3 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | σ ≤ 3% of set time
Phase Y IR (MΩ) | 3 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | σ ≤ 3% of set time
Phase B IR (MΩ) | 3 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | σ ≤ 3% of set time
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-27:2013 Cl.8.4 |  | IR test at 500 VDC – acceptance ≥ 100 MΩ. If < 100 MΩ: stop testing, find fault
IEC 60255-27 Cl.8.3 |  | Earth bond continuity – R < 1 Ω using 4-wire method
IEEE C37.90-2005 Cl.5 |  | Dielectric withstand and insulation resistance for protective relays
NTDC PTW Procedure |  | Permit to Work must be issued before any secondary injection testing. All CTs must be shorted
Siemens 7SA612 Manual |  | Firmware version and settings must match approved setting document G76001-EA087-RSPH1
SEL-421 Instruction Manual |  | Settings verified via AcSELerator Quickset software before testing
SAES-P-111 Sec. 5 |  | Pre-commissioning tests: IR, wiring verification, CT/VT ratio prior to energisation

## Relay Settings Record
RELAY SETTINGS RECORD ¦ 220kV A SUBSTATION–B SUBSTATION ¦ Siemens 7SA612 + SEL-421-5 + Backup 7SJ8021
Standards: IEC 60255-121 ¦ ANSI 21/21N ¦ CT 1200/1 A ¦ VT 220kV/110V (7SA612) / 2000/110V (SEL-421) ¦ Line: 68.50 km
PROCEDURE: Record settings Before (As-Found) and After (As-Left) commissioning. Compare against design setting documents. All secondary Ω values must match the programmed relay settings. Verify against Siemens G76001-EA087-RSPH1 and SEL-421 settings file. KEY FORMULAS: kZE = (Z0−Z1)/(3×Z1) = 0.606 ¦ Z1_sec = Z1_pri × (CT/VT) = Z1_pri × (1/1200)/(110/220000) = Z1_pri × 0.6 ¦ Z1_total_pri = √(R1²+X1²) × L = 0.2867 × 68.5 = 19.64 Ω ¦ VT ratio (7SA612) = 220kV/110V = 2000 ¦ VT ratio (SEL-421) = 2000/110V
A. LINE IMPEDANCE & CT/VT DATA
Parameter |  | Value | Parameter |  | Value | Parameter |  | Value
CT Ratio |  | 1200/1 | VT Ratio (7SA612) |  | 220kV/110V | VT Ratio (SEL-421) |  | 2000/110V
CT Secondary In (A) |  | 1 A | VT Secondary Vn (V) |  | 110 V | Rated Frequency (Hz) |  | 50
Line Length (km) |  | 68.5 | Conductor Type |  | Twin Rail (Zebra ACSR) | Line Angle (°) |  | 83.78
R1 (Ω/km) |  | 0.0311 | X1 (Ω/km) |  | 0.2852 | Z1_pri total (Ω) |  | 19.64
R0 (Ω/km) |  | 0.123 | X0 (Ω/km) |  | 0.8 | Z0_pri total (Ω) |  | 55.44
kZE factor |  | 0.606 | Z0/Z1 ratio |  | 2.82 | Line Angle (°) |  | 83.78°
Z1_sec (Ω) 7SA612 |  | 11.79 | Z0_sec (Ω) 7SA612 |  | 33.27 | Nct/Nvt (7SA612) |  | 0.6
Z1_sec (Ω) SEL-421 |  | 19.65 | Z0_sec (Ω) SEL-421 |  | 55.44 | k0M1 (SEL-421) |  | 0.003
Max. Load Current (A) |  | 1200 | Min. Load Impedance (Ω pri) |  | ≈105 Ω | Load Angle (°) |  | ±45°
B. DISTANCE ZONE SETTINGS — QUADRILATERAL CHARACTERISTIC (Siemens 7SA612 & SEL-421-5)
Zone | Direction | X Ph-Ph (Ω sec) | R Ph-Ph (Ω sec) | X Ph-E (Ω sec) | R Ph-E (Ω sec) | kZE / k0 | Delay (s) | Enable | Remarks
── SIEMENS 7SA612 (PUTT – FCT85) ──
Zone 1 | Forward | 9.97 | 13 | 9.97 | 13.5 | 0.606 | 0 (Inst.) | YES | ≈ 85% line reach
Zone 1B | Forward (SOTF) | 14.06 | 18.25 | 14.06 | 19.65 | 0.606 | 0 (Inst.) | YES | 120% line – SOTF only
Zone 2 | Forward | 14.06 | 18.25 | 14.06 | 19.65 | 0.606 | 0.35 | YES | PUTT send element
Zone 3 | Forward | 17.4 | 19.14 | 17.4 | 20 | 0.606 | 0.7 | YES | Remote backup
Zone 4 | — | INACTIVE | — | — | — | — | — | NO | Not used
Zone 5 | Non-Directional | 22.62 | 22.97 | 22.62 | 24.01 | 0.606 | 2 | YES | Non-directional backup
── SEL-421-5 (POTT SCHEME) ──
Zone 1 | Forward | 6.14 | 7 | 6.14 | 13 | 0.003 (k0M1) | 0 (Inst.) | YES | ≈ 85% line reach
Zone 2 | Forward (POTT) | 8.67 | 9 | 8.67 | 16 | 0.003 (k0M1) | 0.35 | YES | POTT over-reach zone
Zone 3 | — | OFF | OFF | OFF | OFF | — | OFF | NO | Not used
Zone 4 | Forward/POTT | 10.3 | 12 | 10.3 | 30 | 0.003 (k0M1) | 0.7 | YES | Backup/POTT
Zone 5 | — | OFF | OFF | OFF | OFF | — | OFF | NO | Not used
C. SPECIAL FEATURE SETTINGS
Feature | Parameter | Design Setting | 7SA612 As-Found | 7SA612 As-Left | SEL-421 As-Found | SEL-421 As-Left | Remarks
SOTF | Function / ESOTF | ON / Y |  |  |  |  | Closes onto fault – instant trip
SOTF | Zone / SOTFD | Z1B / 10 cyc |  |  |  |  | Active for 10 cycles after CB close
Power Swing | P/S OP Mode / EOOS | Z2-Z5 Blocked / Y1 |  |  |  |  | Blocking during power swing
Power Swing | 68/78 Trip | YES |  |  |  |  | OOS trip enabled
Teleprotection | FCT85 / ECOMM | PUTT / POTT |  |  |  |  | Two-terminal scheme
Teleprotection | Send Element | Zone 1 / Zone 2 |  |  |  |  | Send on Z1 (7SA) / Z2 (SEL)
Stub Protection | 50 Stub Pickup (A sec) | 1.5 A |  |  | N/A | N/A | 7SA612 stub protection
Load Encroachment | Load Encroachment / ELOAD | ON / Y |  |  |  |  | Load blinder active
Load Encroachment | R Load (Ω sec) / ZLF | 14 Ω / 114 Ω
Fuse Failure / LOP | VTFF / ELOP | ON / Y1 |  |  |  |  | Blocks distance on VT fail
Fault Locator | Start / EFLOC | Enabled / Y
Directional Control | E32 | AUTO | N/A | N/A |  |  | SEL-421 auto-select
D. BACKUP OC/EF RELAY SETTINGS — Siemens 7SJ8021-5EB90-1FA0 ¦ CT: 1200/1 A
Element | Parameter |  | Unit | Design Setting | As-Found | As-Left | Primary Value | Remarks
OC (51) | Phase Pickup (In) |  | A sec | 4.5 |  |  | 4.5 × 1200 = 5,400 A | Definite Time
OC (51) | Time Delay (TMS) |  | ms | 800 |  |  | 800 ms | DT – fixed time
OC (51) | Curve Characteristic |  | – | Definite Time |  |  | – | IEC DT
OC (50) | Instantaneous I>> |  | A | BLOCKED | BLOCKED | BLOCKED | – | Not used
EF (51N) | EF Pickup (Io) |  | A sec | 0.11 |  |  | 0.11 × 1200 = 132 A | NI curve – IEC 60255-151
EF (51N) | TMS |  | – | 0.37 |  |  | – | IEC Normal Inverse
EF (51N) | Curve Characteristic |  | – | Normal Inverse (NI) |  |  | – | t=[0.14/((I/Is)^0.02-1)]×TMS
EF (50N) | Instantaneous EF |  | A | BLOCKED | BLOCKED | BLOCKED | – | Not used
General | CT Ratio (Phase/Earth) |  | – | 1200/1 |  |  | –
General | Rated Frequency |  | Hz | 50 |  |  | –
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – RELAY SETTINGS CALCULATION
kZE Calculation |  | kZE = (Z0 − Z1) / (3 × Z1) = (55.42 − 19.65) / (3 × 19.65) = 35.77 / 58.95 = 0.606
Z_secondary (7SA612) |  | Z_sec = Z_pri × (CT_ratio / VT_ratio) = Z_pri × (1200 / (220,000/110)) = Z_pri × 1200/2000 = Z_pri × 0.600
Zone 1 Reach (85% line) |  | Z1_set = 0.85 × Z_line_sec = 0.85 × 11.79 = 10.02 Ω sec (rounded to 9.97 Ω in setting doc)
Zone 1B Reach (120% line) |  | Z1B_set = 1.20 × Z_line_sec = 1.20 × 11.79 = 14.15 Ω sec (7SA612: 14.06 Ω, SEL: 14.15 Ω)
Zone 2 Reach (120% line) |  | Z2_set = 1.20 × Z_line_sec ¦ Acts as PUTT/POTT over-reach element
Zone 3 Reach (~150%) |  | Z3_set ≈ 1.50 × Z_line_sec ¦ Remote backup for next-bus transformer faults
Resistive Reach (R_ph-ph) |  | R_ph-ph ≥ 2 × fault resistance allowance ¦ Set >> load impedance to avoid load encroachment
Load Blinder (7SA612) |  | R_load_min = V_min² / (√3 × S_max) × CT/VT = (220×0.9)² / (√3 × 220000×0.9 × 1200) × 2000 ≈ 14 Ω sec
Load Blinder (SEL-421) |  | ZLF = ZLR = 114 Ω sec ¦ Based on minimum load impedance at maximum load conditions
NI EF Formula |  | t = TMS × [0.14 / ((I/Is)^0.02 − 1)] ¦ e.g. TMS=0.37, I=5×Is: t = 0.37 × [0.14/0.03270] = 1.584 s
k0 (SEL-421) |  | k0M1 = (Z0/Z1 − 1)/3 = (55.44/19.65 − 1)/3 = (2.823−1)/3 = 0.608 ≈ 0.003 (SEL residual comp.)
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 |  | Distance relay settings: zone reach, angle, time delay, directional characteristic
IEC 60255-151:2009 |  | OC/EF relay settings: pickup, TMS, curve selection, definite-time vs IDMT
G76001-EA087-RSPH1 |  | Siemens 7SA612 setting document for 220kV Chakdara-Mardan line (primary reference)
SEL-421 Settings File |  | Settings group S1 – verified via AcSELerator Quickset before commissioning
NTDC Protection Policy |  | Zone reaches: Z1 ≤ 85%, Z2 ≥ 120%, Z3 ≥ 150% of protected line (NTDC-PP-2019)
SAES-P-111 Sec.6.3 |  | Distance relay zone settings: Z1 = 80–85%, Z2 ≥ 115% line impedance
IEEE C37.113-2015 |  | Guide for protective relay applications to transmission lines – zone reach coordination

## Zone 1 (21-Z1)
ZONE 1 REACH ACCURACY & TIMING ¦ ANSI 21-Z1 ¦ IEC 60255-121 ¦ Forward Underreach (~85% Line) ¦ Instantaneous ¦ 220kV A–B
Zone 1 Reach Accuracy & Timing ¦ 7SA612: 9.97 Ω ¦ SEL-421: 10.0 Ω ¦ t ≤ 35 ms
PROCEDURE: (1) Connect test set to relay secondary CT/VT terminals. (2) Set fault angle to 83.78° (current lags voltage). (3) Inject at 90% of set reach → relay MUST OPERATE (operate indication + event log entry). (4) Inject at 110% of set reach → relay must NOT OPERATE (security check). (5) Record measured reach from relay event log / AcSELerator. (6) Zone 1 is instantaneous — record single trip time (must be ≤ 35 ms). FORMULAS: 90% test = 0.90 × Z_set ¦ 110% test = 1.10 × Z_set ¦ Acceptable range = Z_set ± 5% ¦ kZE = 0.606 must be applied for Ph-E faults: Z_measured_PH_E = V_ph / (I_ph + kZE × 3I0) ¦ Trip time: IEC 60255-121 ≤ 35 ms for instantaneous zone. ACCEPTANCE CRITERIA (IEC 60255-121 / ANSI C37.90 / SAES-P-111): Reach accuracy ±5%, trip time ≤ 35 ms, directional security confirmed.
A. SETTINGS & TEST POINT REFERENCE
Parameter | 7SA612 Ph-Ph (Ω sec) |  | 7SA612 Ph-E (Ω sec) |  | SEL-421 Ph-Ph (Ω sec) |  | SEL-421 Ph-E (Ω sec) | Tolerance / Notes
Set Reach (Ω sec) | 9.97 |  | 9.97 |  | 10 |  | 10 | Programmed into relay
90% Test Point (Ω) | 8.973 |  | 8.973 |  | 9 |  | 9 | Inject → relay MUST OPERATE
110% Test Point (Ω) | 10.967 |  | 10.967 |  | 11 |  | 11 | Inject → relay must NOT OPERATE
Acceptable Range (Ω) | 9.472–10.469 |  | 9.472–10.469 |  | 9.5–10.5 |  | 9.5–10.5 | ±5% of Set Reach (IEC 60255-121)
Time Delay | 0 ms (Instantaneous ≤ 35 ms) |  | 0 ms (Instantaneous ≤ 35 ms) |  | 0 ms (Instantaneous ≤ 35 ms) |  | 0 ms (Instantaneous ≤ 35 ms) | Acceptable: set ± 5% or ± 30ms
B. SIEMENS 7SA612 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 9.97 | 8.973 |  | 10.967
B-E (Ph-Earth) | 9.97 | 8.973 |  | 10.967
C-E (Ph-Earth) | 9.97 | 8.973 |  | 10.967
AB (Ph-Ph) | 9.97 | 8.973 |  | 10.967
BC (Ph-Ph) | 9.97 | 8.973 |  | 10.967
CA (Ph-Ph) | 9.97 | 8.973 |  | 10.967
ABC (3-Phase) | 9.97 | 8.973 |  | 10.967
B. SEL-421-5 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 10 | 9 |  | 11
B-E (Ph-Earth) | 10 | 9 |  | 11
C-E (Ph-Earth) | 10 | 9 |  | 11
AB (Ph-Ph) | 10 | 9 |  | 11
BC (Ph-Ph) | 10 | 9 |  | 11
CA (Ph-Ph) | 10 | 9 |  | 11
ABC (3-Phase) | 10 | 9 |  | 11
KEY FORMULAS: Error% = (Meas.Reach − Set Reach) / Set Reach × 100 ¦ Acceptance ±5% (IEC 60255-121) ¦ Fault injection angle = 83.78° (current lags voltage) ¦ kZE = 0.606 (7SA612), k0M1 = 0.003 (SEL-421) ¦ Trip time tolerance: ±5% or ±30ms (whichever greater) ¦ Primary reach = Set Reach_sec / (CT/VT ratio) ¦ 7SA612: CT/VT = (1/1200)/(110/220000) = 0.600 → Z1_sec × (1/0.60) = Z1_pri ¦ SEL-421: CT/VT = (1/1200)/(110/2000000) = (multiply sec by 1666.7 for primary Ω) [VT ratio = 2000/110 = 18.18]
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – Z1 REACH & TIMING ACCURACY
Reach Error % |  | Error% = (Measured_Reach − Set_Reach) / Set_Reach × 100 ¦ Acceptance: ±5% (IEC 60255-121 Cl.7.2)
90% Test Point |  | Z_inject_90% = 0.90 × Z_set = 0.90 × 9.97 = 8.973 Ω sec → relay MUST operate
110% Test Point |  | Z_inject_110% = 1.10 × Z_set = 1.10 × 9.97 = 10.967 Ω sec → relay must NOT operate
Acceptable Range |  | Z_acceptable = Z_set × (1 ± 0.05) = 9.472 Ω to 10.469 Ω (7SA612) ¦ SEL-421: 9.5–10.5 Ω
Trip Time Tol. |  | Instantaneous: T ≤ 35 ms from fault inception (IEC 60255-121 Cl.7.1)
Fault Injection Angle |  | Current must lag voltage by fault angle = 83.78° ¦ Set test-set: angle = 83.78° (line angle = arctan(X1/R1) = arctan(0.2852/0.0311))
Ph-Earth kZE comp. |  | Z_measured_PH_E = V_ph / (I_ph + kZE × 3I₀) ¦ kZE = 0.606 (7SA612) ¦ k0M1 = 0.003 (SEL-421 residual comp.)
Primary Reach |  | Z_primary = Z_sec / (CT/VT) = Z_sec / 0.600 (7SA612) ¦ e.g. Z1_sec=9.97 Ω → Z1_pri = 16.62 Ω
Line Angle |  | Line angle θ = arctan(X1/R1) = arctan(0.2852/0.0311) = arctan(9.17) = 83.78°
Standard Deviation |  | σ = √[Σ(xi − x̄)² / (n−1)] ¦ Coefficient of Variation CoV = σ/x̄ × 100% ¦ Target: σ ≤ 5 ms (instantaneous)
📊 STANDARD DEVIATION ANALYSIS – Z1 TIMING MEASUREMENTS (IEC 60255-121)
Enter 3 timing shots per fault type. Use columns below for automatic σ calculation. Acceptance: σ ≤ 5 ms for instantaneous zones (IEC 60255-121) ¦ σ ≤ 3% of set time for timed zones ¦ CoV > 10% indicates test-set instability or relay pickup margin issue.
Fault Type | T-Shot 1 (ms) | T-Shot 2 (ms) | T-Shot 3 (ms) | Mean x̄ (ms) | Std Dev σ (ms) | Variance σ² | Min (ms) | Max (ms) | CoV (%) / Status
A-E (Ph-Earth) | [8 empty] | –
B-E (Ph-Earth) | [8 empty] | –
C-E (Ph-Earth) | [8 empty] | –
AB (Ph-Ph) | [8 empty] | –
BC (Ph-Ph) | [8 empty] | –
CA (Ph-Ph) | [8 empty] | –
ABC (3-Phase) | [8 empty] | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 Cl.7 |  | Reach accuracy: ±5% ¦ Trip time accuracy: ±5% or ±30ms (whichever greater)
IEC 60255-121 Cl.7.2 |  | Test procedure: inject at 90% (operate) and 110% (non-operate) of set reach
IEC 60255-121 Annex A |  | Measurement uncertainty: test set accuracy must be better than ±1% for reach, ±2ms for timing
ANSI/IEEE C37.90 |  | Relay testing: verify operate and non-operate boundaries, record time to trip
NTDC Guidelines |  | Zone reaches: Z1=85%, Z2=120%, Z3=150%. All zones tested at ≥ 3 fault types each phase
SAES-P-111 Sec.6.4 |  | Distance relay zone tests: reach accuracy ±5%, trip time per IEC 60255-121
IEC 60834-1 |  | PUTT/POTT teleprotection: transfer trip time ≤ 3 × relay operate time + channel delay

## Zone 1B & Z2-POTT
ZONE 1B (SOTF) / ZONE 2 (POTT) REACH ACCURACY & TIMING ¦ ANSI 21-Z1B/Z2 ¦ IEC 60255-121 ¦ Forward Overreach (~120% Line) ¦ 220kV A–B
Zone 1B SOTF (7SA612) & Zone 2 POTT (SEL-421) ¦ 7SA612: 14.06 Ω ¦ SEL-421: 14.15 Ω
PROCEDURE (Zone 1B / SOTF — 7SA612): (1) SOTF Active Test: Open CB → apply fault at 90% of Z1B set reach → close CB → relay MUST TRIP instantly (≤ 35 ms). (2) Without SOTF (CB already closed): relay must NOT trip on Z1B (waits for Z2 timed backup). PROCEDURE (Zone 2 / POTT — SEL-421): (1) Inject at 90% of Z2 reach – relay should operate in 350 ms (timed). (2) Simulate POTT: inject Zone 2 fault AND assert permissive receive signal → relay should trip instantly. FORMULAS: 90% test = 0.90 × Z_set ¦ 110% test = 1.10 × Z_set ¦ Z1B (7SA612) = 14.06 Ω sec ¦ Z2 (SEL-421) = 14.15 Ω sec ¦ Delay tolerance: ±5% or ±30 ms (IEC 60255-121) ¦ POTT trip time = comms delay + Zone 2 operate time (should be < 100 ms total).
A. SETTINGS & TEST POINT REFERENCE
Parameter | 7SA612 Ph-Ph (Ω sec) |  | 7SA612 Ph-E (Ω sec) |  | SEL-421 Ph-Ph (Ω sec) |  | SEL-421 Ph-E (Ω sec) | Tolerance / Notes
Set Reach (Ω sec) | 14.06 |  | 14.06 |  | 14.15 |  | 14.15 | Programmed into relay
90% Test Point (Ω) | 12.654 |  | 12.654 |  | 12.735 |  | 12.735 | Inject → relay MUST OPERATE
110% Test Point (Ω) | 15.466 |  | 15.466 |  | 15.565 |  | 15.565 | Inject → relay must NOT OPERATE
Acceptable Range (Ω) | 13.357–14.763 |  | 13.357–14.763 |  | 13.442–14.858 |  | 13.442–14.858 | ±5% of Set Reach (IEC 60255-121)
Time Delay | 0 ms (SOTF Inst.) / 350 ms (timed) |  | 0 ms (SOTF Inst.) / 350 ms (timed) |  | 350 ms ± 35 ms (timed) / Instant. with POTT Rx |  | 350 ms ± 35 ms (timed) / Instant. with POTT Rx | Acceptable: set ± 5% or ± 30ms
B. SIEMENS 7SA612 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
B-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
C-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
AB (Ph-Ph) | 14.06 | 12.654 |  | 15.466
BC (Ph-Ph) | 14.06 | 12.654 |  | 15.466
CA (Ph-Ph) | 14.06 | 12.654 |  | 15.466
ABC (3-Phase) | 14.06 | 12.654 |  | 15.466
B. SEL-421-5 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 14.15 | 12.735 |  | 15.565
B-E (Ph-Earth) | 14.15 | 12.735 |  | 15.565
C-E (Ph-Earth) | 14.15 | 12.735 |  | 15.565
AB (Ph-Ph) | 14.15 | 12.735 |  | 15.565
BC (Ph-Ph) | 14.15 | 12.735 |  | 15.565
CA (Ph-Ph) | 14.15 | 12.735 |  | 15.565
ABC (3-Phase) | 14.15 | 12.735 |  | 15.565
KEY FORMULAS: Error% = (Meas.Reach − Set Reach) / Set Reach × 100 ¦ Acceptance ±5% (IEC 60255-121) ¦ Fault injection angle = 83.78° (current lags voltage) ¦ kZE = 0.606 (7SA612), k0M1 = 0.003 (SEL-421) ¦ Trip time tolerance: ±5% or ±30ms (whichever greater) ¦ Primary reach = Set Reach_sec / (CT/VT ratio) ¦ 7SA612: CT/VT = (1/1200)/(110/220000) = 0.600 → Z1_sec × (1/0.60) = Z1_pri ¦ SEL-421: CT/VT = (1/1200)/(110/2000000) = (multiply sec by 1666.7 for primary Ω) [VT ratio = 2000/110 = 18.18]
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – Z1B REACH & TIMING ACCURACY
Reach Error % |  | Error% = (Measured_Reach − Set_Reach) / Set_Reach × 100 ¦ Acceptance: ±5% (IEC 60255-121 Cl.7.2)
90% Test Point |  | Z_inject_90% = 0.90 × Z_set = 0.90 × 14.06 = 12.654 Ω sec → relay MUST operate
110% Test Point |  | Z_inject_110% = 1.10 × Z_set = 1.10 × 14.06 = 15.466 Ω sec → relay must NOT operate
Acceptable Range |  | Z_acceptable = Z_set × (1 ± 0.05) = 13.357 Ω to 14.763 Ω (7SA612) ¦ SEL-421: 13.442–14.858 Ω
Trip Time Tol. |  | T_acceptable = T_set ± max(5%, 30ms) = 350 ± 35 ms → range: 315–385 ms
Fault Injection Angle |  | Current must lag voltage by fault angle = 83.78° ¦ Set test-set: angle = 83.78° (line angle = arctan(X1/R1) = arctan(0.2852/0.0311))
Ph-Earth kZE comp. |  | Z_measured_PH_E = V_ph / (I_ph + kZE × 3I₀) ¦ kZE = 0.606 (7SA612) ¦ k0M1 = 0.003 (SEL-421 residual comp.)
Primary Reach |  | Z_primary = Z_sec / (CT/VT) = Z_sec / 0.600 (7SA612) ¦ e.g. Z1_sec=14.06 Ω → Z1_pri = 23.43 Ω
Line Angle |  | Line angle θ = arctan(X1/R1) = arctan(0.2852/0.0311) = arctan(9.17) = 83.78°
Standard Deviation |  | σ = √[Σ(xi − x̄)² / (n−1)] ¦ Coefficient of Variation CoV = σ/x̄ × 100% ¦ Target: σ ≤ 5 ms (instantaneous)
📊 STANDARD DEVIATION ANALYSIS – Z1B TIMING MEASUREMENTS (IEC 60255-121)
Enter 3 timing shots per fault type. Use columns below for automatic σ calculation. Acceptance: σ ≤ 5 ms for instantaneous zones (IEC 60255-121) ¦ σ ≤ 3% of set time for timed zones ¦ CoV > 10% indicates test-set instability or relay pickup margin issue.
Fault Type | T-Shot 1 (ms) | T-Shot 2 (ms) | T-Shot 3 (ms) | Mean x̄ (ms) | Std Dev σ (ms) | Variance σ² | Min (ms) | Max (ms) | CoV (%) / Status
A-E (Ph-Earth) | [8 empty] | –
B-E (Ph-Earth) | [8 empty] | –
C-E (Ph-Earth) | [8 empty] | –
AB (Ph-Ph) | [8 empty] | –
BC (Ph-Ph) | [8 empty] | –
CA (Ph-Ph) | [8 empty] | –
ABC (3-Phase) | [8 empty] | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 Cl.7 |  | Reach accuracy: ±5% ¦ Trip time accuracy: ±5% or ±30ms (whichever greater)
IEC 60255-121 Cl.7.2 |  | Test procedure: inject at 90% (operate) and 110% (non-operate) of set reach
IEC 60255-121 Annex A |  | Measurement uncertainty: test set accuracy must be better than ±1% for reach, ±2ms for timing
ANSI/IEEE C37.90 |  | Relay testing: verify operate and non-operate boundaries, record time to trip
NTDC Guidelines |  | Zone reaches: Z1=85%, Z2=120%, Z3=150%. All zones tested at ≥ 3 fault types each phase
SAES-P-111 Sec.6.4 |  | Distance relay zone tests: reach accuracy ±5%, trip time per IEC 60255-121
IEC 60834-1 |  | PUTT/POTT teleprotection: transfer trip time ≤ 3 × relay operate time + channel delay

## Zone 2 & Z4
ZONE 2 (7SA612) / ZONE 4 (SEL-421) REACH ACCURACY & TIMING ¦ ANSI 21-Z2/Z4 ¦ IEC 60255-121 ¦ Forward Time-Delayed Backup ¦ 220kV A–B
Zone 2 (7SA612) & Zone 4 (SEL-421) ¦ 7SA612: 14.06 Ω / 350 ms ¦ SEL-421: 17.5 Ω / 700 ms
PROCEDURE: (1) Inject fault at 90% of Z2/Z4 set reach → relay must operate after the set time delay. (2) Inject at 110% of set reach → relay must NOT operate (security). (3) Record 3 timing shots and calculate average. (4) Verify time delay accuracy within ±5% or ±30 ms (IEC 60255-121). FORMULAS: 7SA612 Z2 reach = 14.06 Ω sec ¦ SEL-421 Z4 reach = 17.5 Ω sec ¦ 7SA612 Z2 delay = 350 ms ± 35 ms ¦ SEL-421 Z4 delay = 700 ms ± 35 ms ¦ Reach accuracy ±5% ¦ Z2/Z4 serves as remote backup for adjacent line / transformer faults ¦ ACCEPTANCE (IEC 60255-121 / NTDC / SAES-P-111): Reach ±5%, time ±5% or ±30 ms.
A. SETTINGS & TEST POINT REFERENCE
Parameter | 7SA612 Ph-Ph (Ω sec) |  | 7SA612 Ph-E (Ω sec) |  | SEL-421 Ph-Ph (Ω sec) |  | SEL-421 Ph-E (Ω sec) | Tolerance / Notes
Set Reach (Ω sec) | 14.06 |  | 14.06 |  | 17.5 |  | 17.5 | Programmed into relay
90% Test Point (Ω) | 12.654 |  | 12.654 |  | 15.75 |  | 15.75 | Inject → relay MUST OPERATE
110% Test Point (Ω) | 15.466 |  | 15.466 |  | 19.25 |  | 19.25 | Inject → relay must NOT OPERATE
Acceptable Range (Ω) | 13.357–14.763 |  | 13.357–14.763 |  | 16.625–18.375 |  | 16.625–18.375 | ±5% of Set Reach (IEC 60255-121)
Time Delay | 350 ms ± 35 ms |  | 350 ms ± 35 ms |  | 700 ms ± 35 ms |  | 700 ms ± 35 ms | Acceptable: set ± 5% or ± 30ms
B. SIEMENS 7SA612 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
B-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
C-E (Ph-Earth) | 14.06 | 12.654 |  | 15.466
AB (Ph-Ph) | 14.06 | 12.654 |  | 15.466
BC (Ph-Ph) | 14.06 | 12.654 |  | 15.466
CA (Ph-Ph) | 14.06 | 12.654 |  | 15.466
ABC (3-Phase) | 14.06 | 12.654 |  | 15.466
B. SEL-421-5 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 17.5 | 15.75 |  | 19.25
B-E (Ph-Earth) | 17.5 | 15.75 |  | 19.25
C-E (Ph-Earth) | 17.5 | 15.75 |  | 19.25
AB (Ph-Ph) | 17.5 | 15.75 |  | 19.25
BC (Ph-Ph) | 17.5 | 15.75 |  | 19.25
CA (Ph-Ph) | 17.5 | 15.75 |  | 19.25
ABC (3-Phase) | 17.5 | 15.75 |  | 19.25
KEY FORMULAS: Error% = (Meas.Reach − Set Reach) / Set Reach × 100 ¦ Acceptance ±5% (IEC 60255-121) ¦ Fault injection angle = 83.78° (current lags voltage) ¦ kZE = 0.606 (7SA612), k0M1 = 0.003 (SEL-421) ¦ Trip time tolerance: ±5% or ±30ms (whichever greater) ¦ Primary reach = Set Reach_sec / (CT/VT ratio) ¦ 7SA612: CT/VT = (1/1200)/(110/220000) = 0.600 → Z1_sec × (1/0.60) = Z1_pri ¦ SEL-421: CT/VT = (1/1200)/(110/2000000) = (multiply sec by 1666.7 for primary Ω) [VT ratio = 2000/110 = 18.18]
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – Z2 REACH & TIMING ACCURACY
Reach Error % |  | Error% = (Measured_Reach − Set_Reach) / Set_Reach × 100 ¦ Acceptance: ±5% (IEC 60255-121 Cl.7.2)
90% Test Point |  | Z_inject_90% = 0.90 × Z_set = 0.90 × 14.06 = 12.654 Ω sec → relay MUST operate
110% Test Point |  | Z_inject_110% = 1.10 × Z_set = 1.10 × 14.06 = 15.466 Ω sec → relay must NOT operate
Acceptable Range |  | Z_acceptable = Z_set × (1 ± 0.05) = 13.357 Ω to 14.763 Ω (7SA612) ¦ SEL-421: 16.625–18.375 Ω
Trip Time Tol. |  | T_acceptable = T_set ± max(5%, 30ms) = 350 ± 35 ms → range: 315–385 ms
Fault Injection Angle |  | Current must lag voltage by fault angle = 83.78° ¦ Set test-set: angle = 83.78° (line angle = arctan(X1/R1) = arctan(0.2852/0.0311))
Ph-Earth kZE comp. |  | Z_measured_PH_E = V_ph / (I_ph + kZE × 3I₀) ¦ kZE = 0.606 (7SA612) ¦ k0M1 = 0.003 (SEL-421 residual comp.)
Primary Reach |  | Z_primary = Z_sec / (CT/VT) = Z_sec / 0.600 (7SA612) ¦ e.g. Z1_sec=14.06 Ω → Z1_pri = 23.43 Ω
Line Angle |  | Line angle θ = arctan(X1/R1) = arctan(0.2852/0.0311) = arctan(9.17) = 83.78°
Standard Deviation |  | σ = √[Σ(xi − x̄)² / (n−1)] ¦ Coefficient of Variation CoV = σ/x̄ × 100% ¦ Target: σ ≤ 5 ms (instantaneous)
📊 STANDARD DEVIATION ANALYSIS – Z2 TIMING MEASUREMENTS (IEC 60255-121)
Enter 3 timing shots per fault type. Use columns below for automatic σ calculation. Acceptance: σ ≤ 5 ms for instantaneous zones (IEC 60255-121) ¦ σ ≤ 3% of set time for timed zones ¦ CoV > 10% indicates test-set instability or relay pickup margin issue.
Fault Type | T-Shot 1 (ms) | T-Shot 2 (ms) | T-Shot 3 (ms) | Mean x̄ (ms) | Std Dev σ (ms) | Variance σ² | Min (ms) | Max (ms) | CoV (%) / Status
A-E (Ph-Earth) | [8 empty] | –
B-E (Ph-Earth) | [8 empty] | –
C-E (Ph-Earth) | [8 empty] | –
AB (Ph-Ph) | [8 empty] | –
BC (Ph-Ph) | [8 empty] | –
CA (Ph-Ph) | [8 empty] | –
ABC (3-Phase) | [8 empty] | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 Cl.7 |  | Reach accuracy: ±5% ¦ Trip time accuracy: ±5% or ±30ms (whichever greater)
IEC 60255-121 Cl.7.2 |  | Test procedure: inject at 90% (operate) and 110% (non-operate) of set reach
IEC 60255-121 Annex A |  | Measurement uncertainty: test set accuracy must be better than ±1% for reach, ±2ms for timing
ANSI/IEEE C37.90 |  | Relay testing: verify operate and non-operate boundaries, record time to trip
NTDC Guidelines |  | Zone reaches: Z1=85%, Z2=120%, Z3=150%. All zones tested at ≥ 3 fault types each phase
SAES-P-111 Sec.6.4 |  | Distance relay zone tests: reach accuracy ±5%, trip time per IEC 60255-121
IEC 60834-1 |  | PUTT/POTT teleprotection: transfer trip time ≤ 3 × relay operate time + channel delay

## Zone 3 & Z5
ZONE 3 & ZONE 5 (7SA612 ONLY) REACH ACCURACY & TIMING ¦ ANSI 21-Z3/Z5 ¦ IEC 60255-121 ¦ Zone 3: Forward 700ms ¦ Zone 5: Non-Directional 2000ms ¦ 220kV A–B
Zone 3 (17.40 Ω / 700 ms) & Zone 5 Non-Dir (22.62 Ω / 2000 ms) — 7SA612 only
PROCEDURE: (1) Zone 3 (7SA612 Forward, 700 ms): Inject fault at 90% of Z3 reach → relay MUST operate after 700 ms. (2) Zone 5 (7SA612 Non-Directional, 2000 ms): Inject forward and reverse faults → relay must operate in both directions after 2000 ms. (3) Record 3 timing shots for each. FORMULAS: 7SA612 Z3 = 17.40 Ω sec, t = 700 ms ± 35 ms ¦ 7SA612 Z5 = 22.62 Ω sec, t = 2000 ms ± 100 ms ¦ Z3 provides remote backup for next-line Zone 2 faults ¦ Z5 non-directional provides ultimate backup for all faults within impedance reach ¦ Acceptance: Reach ±5%, timing ±5% or ±30 ms (IEC 60255-121 / NTDC guidelines / SAES-P-111).
A. SETTINGS & TEST POINT REFERENCE
Parameter | 7SA612 Ph-Ph (Ω sec) |  | 7SA612 Ph-E (Ω sec) |  | SEL-421 Ph-Ph (Ω sec) |  | SEL-421 Ph-E (Ω sec) | Tolerance / Notes
Set Reach (Ω sec) | 17.4 |  | 17.4 |  | 22.62 |  | 22.62 | Programmed into relay
90% Test Point (Ω) | 15.66 |  | 15.66 |  | 20.358 |  | 20.358 | Inject → relay MUST OPERATE
110% Test Point (Ω) | 19.14 |  | 19.14 |  | 24.882 |  | 24.882 | Inject → relay must NOT OPERATE
Acceptable Range (Ω) | 16.53–18.27 |  | 16.53–18.27 |  | 21.489–23.751 |  | 21.489–23.751 | ±5% of Set Reach (IEC 60255-121)
Time Delay | 700 ms ± 35 ms (Z3) / 2000 ms ± 100 ms (Z5) |  | 700 ms ± 35 ms (Z3) / 2000 ms ± 100 ms (Z5) |  | N/A (SEL-421 Z3 & Z5 = OFF) |  | N/A (SEL-421 Z3 & Z5 = OFF) | Acceptable: set ± 5% or ± 30ms
B. SIEMENS 7SA612 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 17.4 | 15.66 |  | 19.14
B-E (Ph-Earth) | 17.4 | 15.66 |  | 19.14
C-E (Ph-Earth) | 17.4 | 15.66 |  | 19.14
AB (Ph-Ph) | 17.4 | 15.66 |  | 19.14
BC (Ph-Ph) | 17.4 | 15.66 |  | 19.14
CA (Ph-Ph) | 17.4 | 15.66 |  | 19.14
ABC (3-Phase) | 17.4 | 15.66 |  | 19.14
B. SEL-421-5 — REACH ACCURACY TEST (Fault Angle = 83.78°)
Fault Type | Set Reach (Ω sec) | 90% Test (Ω sec) | Operated (Y/N) | 110% Test (Ω sec) | No-Op (Y/N) | Meas. Reach (Ω sec) | Error (%) | Time (ms) | Pass/Fail
A-E (Ph-Earth) | 22.62 | 20.358 |  | 24.882
B-E (Ph-Earth) | 22.62 | 20.358 |  | 24.882
C-E (Ph-Earth) | 22.62 | 20.358 |  | 24.882
AB (Ph-Ph) | 22.62 | 20.358 |  | 24.882
BC (Ph-Ph) | 22.62 | 20.358 |  | 24.882
CA (Ph-Ph) | 22.62 | 20.358 |  | 24.882
ABC (3-Phase) | 22.62 | 20.358 |  | 24.882
KEY FORMULAS: Error% = (Meas.Reach − Set Reach) / Set Reach × 100 ¦ Acceptance ±5% (IEC 60255-121) ¦ Fault injection angle = 83.78° (current lags voltage) ¦ kZE = 0.606 (7SA612), k0M1 = 0.003 (SEL-421) ¦ Trip time tolerance: ±5% or ±30ms (whichever greater) ¦ Primary reach = Set Reach_sec / (CT/VT ratio) ¦ 7SA612: CT/VT = (1/1200)/(110/220000) = 0.600 → Z1_sec × (1/0.60) = Z1_pri ¦ SEL-421: CT/VT = (1/1200)/(110/2000000) = (multiply sec by 1666.7 for primary Ω) [VT ratio = 2000/110 = 18.18]
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – Z3 REACH & TIMING ACCURACY
Reach Error % |  | Error% = (Measured_Reach − Set_Reach) / Set_Reach × 100 ¦ Acceptance: ±5% (IEC 60255-121 Cl.7.2)
90% Test Point |  | Z_inject_90% = 0.90 × Z_set = 0.90 × 17.4 = 15.66 Ω sec → relay MUST operate
110% Test Point |  | Z_inject_110% = 1.10 × Z_set = 1.10 × 17.4 = 19.14 Ω sec → relay must NOT operate
Acceptable Range |  | Z_acceptable = Z_set × (1 ± 0.05) = 16.53 Ω to 18.27 Ω (7SA612) ¦ SEL-421: 21.489–23.751 Ω
Trip Time Tol. |  | T_acceptable = T_set ± max(5%, 30ms) = 700 ± 35 ms → range: 665–735 ms
Fault Injection Angle |  | Current must lag voltage by fault angle = 83.78° ¦ Set test-set: angle = 83.78° (line angle = arctan(X1/R1) = arctan(0.2852/0.0311))
Ph-Earth kZE comp. |  | Z_measured_PH_E = V_ph / (I_ph + kZE × 3I₀) ¦ kZE = 0.606 (7SA612) ¦ k0M1 = 0.003 (SEL-421 residual comp.)
Primary Reach |  | Z_primary = Z_sec / (CT/VT) = Z_sec / 0.600 (7SA612) ¦ e.g. Z1_sec=17.4 Ω → Z1_pri = 29.0 Ω
Line Angle |  | Line angle θ = arctan(X1/R1) = arctan(0.2852/0.0311) = arctan(9.17) = 83.78°
Standard Deviation |  | σ = √[Σ(xi − x̄)² / (n−1)] ¦ Coefficient of Variation CoV = σ/x̄ × 100% ¦ Target: σ ≤ 5 ms (instantaneous)
📊 STANDARD DEVIATION ANALYSIS – Z3 TIMING MEASUREMENTS (IEC 60255-121)
Enter 3 timing shots per fault type. Use columns below for automatic σ calculation. Acceptance: σ ≤ 5 ms for instantaneous zones (IEC 60255-121) ¦ σ ≤ 3% of set time for timed zones ¦ CoV > 10% indicates test-set instability or relay pickup margin issue.
Fault Type | T-Shot 1 (ms) | T-Shot 2 (ms) | T-Shot 3 (ms) | Mean x̄ (ms) | Std Dev σ (ms) | Variance σ² | Min (ms) | Max (ms) | CoV (%) / Status
A-E (Ph-Earth) | [8 empty] | –
B-E (Ph-Earth) | [8 empty] | –
C-E (Ph-Earth) | [8 empty] | –
AB (Ph-Ph) | [8 empty] | –
BC (Ph-Ph) | [8 empty] | –
CA (Ph-Ph) | [8 empty] | –
ABC (3-Phase) | [8 empty] | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 Cl.7 |  | Reach accuracy: ±5% ¦ Trip time accuracy: ±5% or ±30ms (whichever greater)
IEC 60255-121 Cl.7.2 |  | Test procedure: inject at 90% (operate) and 110% (non-operate) of set reach
IEC 60255-121 Annex A |  | Measurement uncertainty: test set accuracy must be better than ±1% for reach, ±2ms for timing
ANSI/IEEE C37.90 |  | Relay testing: verify operate and non-operate boundaries, record time to trip
NTDC Guidelines |  | Zone reaches: Z1=85%, Z2=120%, Z3=150%. All zones tested at ≥ 3 fault types each phase
SAES-P-111 Sec.6.4 |  | Distance relay zone tests: reach accuracy ±5%, trip time per IEC 60255-121
IEC 60834-1 |  | PUTT/POTT teleprotection: transfer trip time ≤ 3 × relay operate time + channel delay

## Backup OC-EF (7SJ8021)
BACKUP OVERCURRENT & EARTH FAULT RELAY TESTING ¦ Siemens 7SJ8021-5EB90-1FA0 ¦ ANSI 51/51N ¦ IEC 60255-151
220kV A – B ¦ CT: 1200/1 A ¦ OC Pickup: 4.5 A sec (DT 800ms) ¦ EF Pickup: 0.11 A sec (NI, TMS=0.37)
THEORY: Overcurrent protection (ANSI 51) provides backup protection for faults not cleared by distance relays. The Siemens 7SJ8021 relay provides: (A) Phase OC – Definite Time (DT) at 4.5 A sec (= 5,400 A primary) with 800 ms delay; (B) Earth Fault OC – Normal Inverse (NI) curve with pickup 0.11 A sec (= 132 A primary), TMS = 0.37. FORMULAS: DT OC: Trip time = T_set = 800 ms (constant regardless of fault magnitude) ¦ NI EF: t = TMS × [0.14 / ((I/Is)^0.02 − 1)] where I = injected current, Is = 0.11 A ¦ Primary OC pickup = I_set(sec) × CT = 4.5 × 1200 = 5,400 A ¦ Primary EF pickup = 0.11 × 1200 = 132 A ¦ Pickup tolerance: ±5% (IEC 60255-151) ¦ Time tolerance: ±5% or ±30 ms (whichever greater) ¦ Drop-off (reset) ratio: ≥ 0.95 × pickup ¦ STANDARDS: IEC 60255-151, IEC 60255-27, ANSI/IEEE C37.90, NTDC/WAPDA Guidelines, SAES-P-111.
A. OVERCURRENT PICKUP / OPERATE CURRENT TEST (IEC 60255-151 Cl.5)
Phase | Set Pickup (A sec) | 102% – Should Operate (A) | Measured Operate (A) | 98% – Should NOT Operate (A) | Measured No-Op (A) | Drop-off (95%) (A) | Meas. Drop-off (A) | Pass/Fail | Remarks
Phase A (R) | 4.5 | 4.59 |  | 4.41 |  | 4.275
Phase B (Y) | 4.5 | 4.59 |  | 4.41 |  | 4.275
Phase C (B) | 4.5 | 4.59 |  | 4.41 |  | 4.275
B. OVERCURRENT TIMING TEST – DEFINITE TIME (DT 800 ms) (IEC 60255-151 Cl.5) ¦ Formula: t = T_set = 800 ms (constant)
Test No. | Test Description | Test Current (× In) | Applied Current (A) | Calc. Trip Time (s) | Meas. Trip Time-1 (s) | Meas. Trip Time-2 (s) | Meas. Trip Time-3 (s) | Average (s) | Pass/Fail
OC-1 | Pickup verification Ph-A | 1.0× | 4.5 | PICK-UP (no trip)
OC-2 | DT @ 2× pickup – Phase A | 2.0× | 9 | 0.8 |  |  |  | #DIV/0!
OC-3 | DT @ 3× pickup – Phase A | 3.0× | 13.5 | 0.8
OC-4 | DT @ 5× pickup – Phase A | 5.0× | 22.5 | 0.8
OC-5 | 3-Phase simultaneous @ 5× | 5.0× | 22.5 | 0.8
OC-6 | Phase B – 5× pickup | 5.0× | 22.5 | 0.8
OC-7 | Phase C – 5× pickup | 5.0× | 22.5 | 0.8
OC-8 | Reset / drop-off verification | 0.95× | 4.275 | RELAY RESETS
C. EARTH FAULT PICKUP TEST (51N) ¦ Pickup = 0.11 A sec ¦ Primary = 132 A
Element | Set Pickup (A sec) | 102% – Operate (A) | Measured Operate (A) | 98% – No-Op (A) | Measured No-Op (A) | Drop-off (0.1045 A) | Meas. Drop-off (A) | Pass/Fail | Remarks
51N – Earth Fault | 0.11 | 0.1122 |  | 0.1078 |  | 0.1045
50N – Inst. EF | BLOCKED | BLOCKED | BLOCKED | BLOCKED | BLOCKED | BLOCKED | BLOCKED
D. EARTH FAULT TIMING TEST – NORMAL INVERSE (NI) ¦ t = TMS × [0.14 / ((I/Is)^0.02 − 1)] ¦ TMS=0.37, Is=0.11 A
Test No. | Test (× Io) | Applied (A) | Calc. Trip Time (s) | Step-by-Step Calc. | Meas. Time-1 (s) | Meas. Time-2 (s) | Meas. Time-3 (s) | Avg. (s) | Pass/Fail
EF-1 | Pickup | 0.11 | PICK-UP | M=1 → no trip (at threshold)
EF-2 | 2× Io | 0.22 | 3.711 | M=2; 2^0.02=1.01396; 0.14/(1.01396-1)=10.03; ×0.37=3.71s
EF-3 | 3× Io | 0.33 | 2.332 | M=3; 3^0.02=1.02227; 0.14/0.02227=6.29; ×0.37=2.33s
EF-4 | 5× Io | 0.55 | 1.583 | M=5; 5^0.02=1.03270; 0.14/0.03270=4.28; ×0.37=1.58s
EF-5 | 10× Io | 1.1 | 1.099 | M=10; 10^0.02=1.04713; 0.14/0.04713=2.97; ×0.37=1.10s
EF-6 | Reset | 0.1045 | RELAY RESETS | Drop-off ≈ 0.95 × Is = 0.1045 A
E. OUTPUT RELAY / INTEGRATION CHECKS
1 | Trip output relay contacts (T4) energised on phase OC trip
2 | Trip contacts energised on EF (51N) trip
3 | LED indicators: 'TRIP' and 'PICKUP' illuminate correctly
4 | Event record shows correct fault type, current, and trip time
5 | Binary BLOCK input verified – inhibits trip correctly
6 | Wiring continuity from CT to relay and relay to trip coil confirmed
7 | CB Trip confirmed – Phase O/C at 3× In
8 | CB Trip confirmed – Earth Fault at 3× Io
9 | Trip Circuit Supervision (TCS) alarm confirmed on open coil
10 | Auxiliary supply variation test (±10%) – relay healthy
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – OVERCURRENT & EARTH FAULT PROTECTION (IEC 60255-151)
IEC Normal Inverse (NI) |  | t = TMS × [0.14 / ((I/Is)^0.02 − 1)] ¦ where: I = injected current (A sec), Is = pickup (A sec), TMS = time multiplier
NI Step-by-Step @2×Is |  | M = I/Is = 2 ¦ M^α = 2^0.02 = 1.01396 ¦ denom = 0.01396 ¦ t = TMS × (0.14/0.01396) = TMS × 10.031 ¦ @TMS=0.37: t=3.711 s
NI Step-by-Step @5×Is |  | M = 5 ¦ 5^0.02 = 1.03270 ¦ denom = 0.03270 ¦ t = TMS × (0.14/0.03270) = TMS × 4.281 ¦ @TMS=0.37: t=1.584 s
NI Step-by-Step @10×Is |  | M = 10 ¦ 10^0.02 = 1.04713 ¦ denom = 0.04713 ¦ t = TMS × (0.14/0.04713) = TMS × 2.970 ¦ @TMS=0.37: t=1.099 s
IEC Very Inverse (VI) |  | t = TMS × [13.5 / ((I/Is) − 1)] ¦ (not used here – reference only)
IEC Extremely Inverse |  | t = TMS × [80 / ((I/Is)² − 1)] ¦ (not used here – reference only)
Definite Time OC |  | t = T_set = 800 ms (constant regardless of fault magnitude) ¦ Primary pickup = 4.5 × 1200 = 5,400 A
Primary EF Pickup |  | I_EF_primary = Is_sec × CT_ratio = 0.11 × 1200 = 132 A ¦ 22% × In_primary (sensitive EF setting)
Pickup Tolerance |  | Acceptable pickup = Is × (1 ± 0.05) → 0.11 × 0.95 = 0.1045 A to 0.11 × 1.05 = 0.1155 A
Time Tolerance (IEC) |  | ΔT_accept = max(5% of T_calc, 30 ms) ¦ e.g. T=3.711s: ΔT = max(0.186s, 30ms) = 186ms ¦ Acceptable: 3.525–3.897 s
Drop-off Ratio |  | Drop-off current ≈ 0.95 × Is_pickup ¦ OC: 0.95 × 4.5 = 4.275 A ¦ EF: 0.95 × 0.11 = 0.1045 A
Standard Deviation (σ) |  | σ = √[Σ(ti − t̄)² / (n−1)] ¦ n=3 shots minimum ¦ Acceptance: σ ≤ max(3% T_calc, 30ms)
📊 STANDARD DEVIATION ANALYSIS – OC/EF TIMING MEASUREMENTS
Enter 3 timing shots per test. Formulas calculate Mean, σ, Variance automatically. Acceptance per IEC 60255-151: timing tolerance = ±max(5%, 30ms). σ > 50ms for DT relay or σ > 200ms for NI relay indicates relay or test-set fault.
Test ID | T-Shot 1 (s) | T-Shot 2 (s) | T-Shot 3 (s) | Calc. Time (s) | Mean x̄ (s) | Std Dev σ (s) | Tol. (±s) | Status | Remarks
OC-2 (DT, 2×In) |  |  |  | 0.8 |  |  | ±0.040 | –
OC-3 (DT, 3×In) |  |  |  | 0.8 |  |  | ±0.040 | –
OC-4 (DT, 5×In) |  |  |  | 0.8 |  |  | ±0.040 | –
EF-2 (NI, 2×Io) |  |  |  | 3.711 |  |  | ±0.186 | –
EF-3 (NI, 3×Io) |  |  |  | 2.328 |  |  | ±0.117 | –
EF-4 (NI, 5×Io) |  |  |  | 1.584 |  |  | ±0.079 | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-151:2009 Cl.5 |  | IDMT overcurrent: pickup ±5%, timing ±5% or ±30ms of calculated trip time
IEC 60255-151 Cl.7 |  | Definite time overcurrent: pickup ±5%, time accuracy ±1% or ±25ms
IEC 60255-151 Annex B |  | IEC curve equations: NI, VI, EI, LTI – coefficients and exponents (α=0.02 for NI)
IEC 60255-27 Cl.8.4 |  | Pre-test IR ≥ 100 MΩ at 500 VDC for all circuits
ANSI/IEEE C37.112-1996 |  | IEEE standard inverse-time characteristic equations for overcurrent relays
NTDC OC/EF Policy |  | Backup OC: DT at 4.5A/800ms (phase), NI at 0.11A TMS=0.37 (earth fault) – per NTDC grading study
7SJ8021 Manual Sec.5 |  | Relay characteristic curves, pickup accuracy, reset time, binary I/O operation
SAES-P-111 Sec.6.5 |  | Overcurrent relay coordination: grading time 300–400 ms between successive zones

## Teleprotection PUTT-POTT
TELEPROTECTION TEST ¦ 7SA612: PUTT (FCT85) ¦ SEL-421: POTT (COMM) ¦ ANSI 85 ¦ IEC 60834-1
220kV A–B ¦ Two-Terminal Scheme ¦ 7SA612: Send=Z1, Rcv+Z2→Inst. ¦ SEL-421: Send=Z2, POTT Rcv→Inst.
THEORY: PUTT (Permissive Under-reach Transfer Trip): Chakdara end sends a permissive signal when Zone 1 operates. Mardan end: if Z2 picks up AND permissive received → instantaneous trip. Without Rx signal: Mardan trips on Z2 time delay (350 ms). POTT (Permissive Over-reach Transfer Trip – SEL-421): Both ends send permissive if Z2 picks up. If both ends receive permissive AND Zone 2 operates → instantaneous trip. PROCEDURE: (1) Apply Z1 fault at Chakdara end – verify FCT85/COMM send signal asserted. (2) Apply Z2 fault at Mardan end with Rx signal simulated – verify instantaneous trip (< comms delay + 30 ms). (3) Apply Z2 fault WITHOUT Rx – verify relay trips on Z2 time delay (350 ms). (4) Test channel guard: remove signal – verify guard alarm raised. FORMULAS: PUTT trip time = channel propagation delay + relay operate time ≈ < 80 ms ¦ IEC 60834-1: transfer trip time ≤ 3 × relay operate time with comms ¦ Security: no unwanted trip with Rx signal asserted but no fault.
A. CHANNEL HEALTHINESS CHECKS
# | Check Item |  |  | Expected Result |  | Actual Result | Pass/Fail | Initials | Remarks
1 | FCT85 / POTT COMM channel link healthy – no alarm |  |  | Comms active, no guard alarm
2 | GPS / IRIG-B time sync confirmed at both ends |  |  | Time sync active
3 | Channel loopback test – signal sent and received |  |  | Loopback OK
4 | Channel propagation delay measured and recorded |  |  | Record delay (ms)
5 | Guard signal present when no trip command active |  |  | Guard asserted
6 | Channel carrier / pilot frequency confirmed |  |  | Correct frequency
B. PUTT / POTT FUNCTIONAL TEST MATRIX
Test No. | Test Description | Relay | Injected Fault | Rx Signal (Y/N) | Expected Action | Actual Action | Time (ms) | Pass/Fail | Remarks
TP-1 | Z1 fault at Chakdara – verify Tx send | 7SA612 | Z1 fault (90% Z1) | — | FCT85 Tx asserted
TP-2 | Z1 fault – SEL Z2 picks up + Rx assert → instant trip | SEL-421 | Z2 fault + Rx=Y | YES | Instant trip < 80 ms |  |  |  | POTT
TP-3 | Z2 fault WITHOUT Rx – timed backup | 7SA612 | Z2 fault (90%) | NO | Trip @ 350 ms ± 35 ms |  |  |  | Time backup
TP-4 | Z2 fault without Rx – SEL-421 timed backup | SEL-421 | Z2 fault (90%) | NO | Trip @ 350 ms ± 35 ms
TP-5 | Security: Rx asserted, no fault – no trip | Both | No fault | YES | NO TRIP (security) |  | —
TP-6 | Channel guard loss – verify alarm raised | Both | Remove carrier | — | Guard alarm raised |  | —
TP-7 | End-to-End: Chakdara Z1 trip → Mardan instant trip via PUTT | Both | Z1 fault @ CKD | AUTO | Mardan trips instantly |  |  |  | End-to-end
TP-8 | Stub protection (50 Stub) – 7SA612 only | 7SA612 | 1.5 A (stub) | — | Trip @ 100 ms |  |  |  | ANSI 50S
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – TELEPROTECTION PUTT / POTT (IEC 60834-1)
PUTT Trip Time |  | T_PUTT = T_channel + T_Z1_operate ¦ T_channel = propagation delay (measure during test) ¦ Target: < 80 ms total
POTT Trip Time |  | T_POTT = T_channel + T_Z2_operate ¦ Z2 timed trip (no Rx): 350 ms ± 35 ms ¦ With Rx: instant (< 80 ms)
Channel Delay |  | Propagation delay = D_km / (speed of light × VF) ¦ For 68.5 km OPGW: ≈ 0.34 ms one-way ¦ Measure actual at site
IEC 60834-1 Req. |  | Transfer trip time ≤ 3 × relay operate time ¦ Security: no unwanted trip probability < 10⁻⁶/year
PUTT Logic |  | IF (Z1_CKD = 1 AND Rx_MRD = 1 AND Z2_MRD = 1) → Instant trip at Mardan end
POTT Logic |  | IF (Z2_CKD = 1 AND Z2_MRD = 1 AND Rx_CKD = 1 AND Rx_MRD = 1) → Instant trip both ends
Stub Protection |  | 50_Stub: Pickup = 1.5 A sec ¦ Delay = 100 ms ¦ Operates when CB open and fault detected
Security Check |  | With Rx asserted, NO fault: relay must NOT trip. Probability of unwanted trip < IEC 60834-1 threshold
σ Teleprotection |  | σ_trip = √(σ_channel² + σ_relay²) ¦ σ_relay (instantaneous) ≤ 5 ms ¦ Total σ ≤ 10 ms recommended
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60834-1:1999 |  | Teleprotection equipment: performance requirements, transfer trip time, security, dependability
IEC 60834-2:1997 |  | Teleprotection via digital communication channels – performance requirements
IEC 60255-121:2019 |  | Distance relay PUTT/POTT testing procedure and acceptance criteria
IEEE C37.113-2015 Sec.9 |  | Teleprotection schemes: PUTT, POTT, DUTT, blocking – testing guidance
NTDC Teleprotection Std |  | FCT85 pilot wire test: channel healthy, delay measured, end-to-end trip confirmed
Siemens FCT85 Manual |  | FCT85 PUTT configuration: Send=Z1, Receive → Z2+Rx instant trip
SEL-421 POTT Manual |  | ECOMM=POTT: Z2 send, POTT receive → instant trip. SOTFD=10 cyc window
SAES-P-111 Sec.6.6 |  | Pilot protection schemes: transfer trip time ≤ 100 ms, channel continuity monitored

## PSB & Load Encroachment
POWER SWING BLOCKING / OOS (ANSI 68/78) & LOAD ENCROACHMENT (21LE) ¦ IEC 60255-121 ¦ 220kV A–B
7SA612: PSB blocks Z2-Z5 during swing ¦ SEL-421: OOS (EOOS=Y1) ¦ Both: Load blinder active ¦ Line: 68.50 km
THEORY: Power Swing Blocking (PSB/OOS): During a power swing, the impedance locus sweeps across the distance relay characteristic. PSB detects the rate of change of impedance (dZ/dt) and blocks distance zones to prevent unwanted tripping. 7SA612: Blocks Z2-Z5 during swing. OOS trip on P/S enabled. SEL-421: OOS protection enabled (EOOS=Y1), zones 1-4 blocked during out-of-step. Load Encroachment: Prevents distance relay operation on heavy load conditions. 7SA612: R_Load = 14 Ω sec (ZMin primary ≈ 44,957 Ω). SEL-421: ZLF=ZLR=114 Ω, ±45.6°. PROCEDURE: (1) PSB: Ramp impedance into relay characteristic slowly (simulating swing) – verify relay blocked. (2) OOS: Apply impedance trajectory that crosses characteristic – verify OOS trip. (3) Load Encroachment: Apply load impedance in blinder region – relay must NOT trip. FORMULAS: Minimum load impedance (Ω primary) = V² / S = (220,000)² / (√3 × S) ¦ Load blinder: Z_load > R_load setting → no trip ¦ PSB detection: ¦dZ/dt¦ > threshold → swing detected → zones blocked.
A. POWER SWING / OOS SETTINGS RECORD
7SA612 PSB Mode |  | 7SA612 OOS Trip |  | Enabled
SEL-421 EOOS Setting |  | SEL-421 Blocked Zones |  | Z1-Z4 (OOSB1-4=Y)
PSB Detection Method |  | OOS Trip Condition |  | Impedance crosses characteristic
B. POWER SWING BLOCKING TEST MATRIX
Test No. | Test Description | Relay | Impedance Trajectory | Rate of Change | Expected Action | Actual Action | Trip (Y/N) | Pass/Fail | Remarks
PSB-1 | Slow impedance ramp – swing simulation | Both | Z sweeps into Z2 slowly | Low dZ/dt | PSB activates – No trip |  |  |  | Swing detected
PSB-2 | Fast impedance change – genuine fault | Both | Step change into Z1 | High dZ/dt (fast) | Distance trip – no PSB block |  |  |  | Fault ≠ swing
PSB-3 | OOS trip – impedance crosses characteristic | Both | Full swing crossing Z1 | Swing complete | OOS trip activated
PSB-4 | Zone 1 unblocked during PSB | 7SA612 | Z1 fault during swing | — | Z1 still trips (unblocked) |  |  |  | Z1 always trips
C. LOAD ENCROACHMENT / LOAD BLINDER TEST
Test No. | Test Description | Relay | Impedance Applied | Load Angle (°) | Expected Result | Actual Result | Pass/Fail | Remarks
LE-1 | Load impedance inside blinder – no trip | 7SA612 | 14 Ω sec (boundary) | 83.78° | NO TRIP (blinder active) |  |  | R_Load boundary
LE-2 | Load impedance inside blinder – no trip | SEL-421 | 114 Ω (ZLF boundary) | ±45.6° | NO TRIP (blinder active)
LE-3 | Fault inside blinder area – distance trips | Both | Z1 reach (fault) | 83.78° | TRIP – fault detected |  |  | Fault overrides blinder
LE-4 | Heavy load: 1200 A @ 0.9 pf – no trip | Both | ≈ 105 Ω primary | 25.8° | NO TRIP (load) |  |  | Max load condition
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – POWER SWING BLOCKING & LOAD ENCROACHMENT (IEC 60255-121)
PSB Detection |  | dZ/dt = ΔZ / Δt ¦ If dZ/dt < threshold → swing detected → zones blocked ¦ If dZ/dt > threshold → fault → zones operate
Swing Impedance |  | Z_swing(t) = V_source / I_swing ¦ During swing, Z traces ellipse in R-X plane at slip frequency f_slip
Slip Frequency |  | f_slip = ¦f_A − f_B¦ ¦ Power swing: f_slip < 5 Hz ¦ PSB blocking threshold set for slow swings
Min Load Z (pri) |  | Z_load_min = V_min² / S_max = (220×0.9)² / (250×10⁶) = (198)² / 250×10⁶ = 156.8 Ω primary
Load Blinder (sec) |  | Z_load_sec = Z_load_pri × (CT/VT) = 156.8 × 0.600 = 94.1 Ω ¦ 7SA612 R_Load=14Ω (conservative), SEL-421 ZLF=114Ω
Load Angle |  | φ_load = arccos(PF) = arccos(0.9) = 25.8° ¦ Max: arccos(0.8) = 36.9° ¦ Load blinder angle set to ≥ 40°
OOS Trip Condition |  | OOS trip after Z locus crosses inner boundary: Z inside Z1 for > T_OOS → trip (prevents generator damage)
Load Encroachment |  | Relay blocks if Z_measured within blinder AND angle outside fault angle range ¦ Prevents trip on heavy load
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 60255-121:2019 Cl.8 |  | Power swing detection and blocking test requirements
IEEE C37.113-2015 Sec.7 |  | Power swing and out-of-step protection for transmission lines
IEEE C37.102-2006 |  | Guide for AC generator protection – OOS implications for distance relays
NTDC PSB Policy |  | 7SA612 PSB: blocks Z2-Z5 during swing. Z1 unblocked. OOS trip enabled after 3 pole swings
SEL-421 OOS Manual |  | EOOS=Y1: zones 1-4 blocked during OOS. OOS trip enabled after complete impedance traversal
SAES-P-111 Sec.6.7 |  | Power swing blocking required on EHV (≥ 115 kV) lines. Load blinder mandatory at high loading

## CT & VT Checks
CT & VT CHECKS ¦ Polarity, Ratio, Knee Point, Magnetisation ¦ IEC 61869 ¦ 220kV A–B
CT: 1200/1 A ¦ VT: 220kV/110V (7SA612) / 2000V/110V (SEL-421) ¦ Standards: IEC 61869-2, IEC 61869-3, BS 3938, NTDC Guidelines
THEORY: Current Transformers (CTs) convert primary line current to secondary (1 A or 5 A) for relay operation. IEC 61869-2 defines accuracy classes (5P, 10P) and accuracy limit factors (ALF). CT Accuracy Class 5P20: 5% composite error at 20× rated current. Knee Point Voltage (Vk): EMF at which a 10% increase causes 50% increase in magnetising current. Formula: Vk ≥ I_fault × (Rct + Rburden) × ALF ¦ POLARITY: P1→S1 polarity must be maintained. IEC: P1/P2 → S1/S2. Polarity error causes differential relay maloperation. RATIO CHECK: Ratio error = (Actual ratio − Nameplate ratio) / Nameplate ratio × 100 ¦ Acceptance: ±0.5% to ±3% per class. VT CHECKS: VT ratio error ≤ ±0.5% for class 0.5. Phase angle error ≤ 20 minutes. STANDARDS: IEC 61869-2 (CTs), IEC 61869-3 (VTs), BS 3938, NTDC/WAPDA guidelines, Saudi Aramco SAES-P-111.
A. CT RATIO TEST (IEC 61869-2)
CT Tag | Core No. | Nameplate Ratio | Test Primary (A) | Measured Secondary (A) | Calculated Ratio | Ratio Error (%) | Acceptance | Pass/Fail | Remarks
CT – Phase R | Core 1 (Relay) | 1200/1 | 120 |  | 0 |  | ±3%
CT – Phase Y | Core 1 (Relay) | 1200/1 | 120 |  |  |  | ±3%
CT – Phase B | Core 1 (Relay) | 1200/1 | 120 |  |  |  | ±3%
CT – Neutral/EF | Core 2 (EF) | 1200/1 | 120 |  |  |  | ±3%
B. CT POLARITY CHECK
CT Tag | Method | P1 Terminal | S1 Terminal | Polarity Mark | Kick Direction | Expected | Pass/Fail | Remarks
CT – Phase R | DC kick test | P1 | S1 | P1→S1 +ve | Galvanometer deflects +ve on connect | Positive deflection
CT – Phase Y | DC kick test | P1 | S1 | P1→S1 +ve | Galvanometer deflects +ve on connect | Positive deflection
CT – Phase B | DC kick test | P1 | S1 | P1→S1 +ve | Galvanometer deflects +ve on connect | Positive deflection
CT – Neutral | DC kick test | P1 | S1 | P1→S1 +ve | Galvanometer deflects +ve on connect | Positive deflection
C. CT KNEE POINT VOLTAGE & MAGNETISATION TEST (IEC 61869-2)
CT Tag | Core/Class | Nameplate Vk (V) | Measured Vk (V) | Mag. Current @ Vk (mA) | Mag. @ 0.5Vk (mA) | Acceptance | Pass/Fail | Remarks
CT Ph-R | 5P20 | ≥ 400 V |  |  |  | Vk_meas ≥ Vk_nameplate
CT Ph-Y | 5P20 | ≥ 400 V |  |  |  | Vk_meas ≥ Vk_nameplate
CT Ph-B | 5P20 | ≥ 400 V |  |  |  | Vk_meas ≥ Vk_nameplate
CT Neutral | 5P20 | ≥ 400 V |  |  |  | Vk_meas ≥ Vk_nameplate
D. VT RATIO, POLARITY & BURDEN TEST (IEC 61869-3)
VT Tag | Relay | Nameplate Ratio | Primary Applied (V) | Meas. Secondary (V) | Ratio Error (%) | Phase Angle Error (min) | Polarity | Pass/Fail | Remarks
VT Ph-R | 7SA612 | 220kV/110V (2000:1) | 110 (sec) |  |  |  | P1→S1 verified
VT Ph-Y | 7SA612 | 220kV/110V (2000:1) | 110 (sec) |  |  |  | P1→S1 verified
VT Ph-B | 7SA612 | 220kV/110V (2000:1) | 110 (sec) |  |  |  | P1→S1 verified
VT (SEL-421 Y) | SEL-421 | 2000/110V | 110 (sec) |  |  |  | P1→S1 verified
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – CT & VT TESTING (IEC 61869-2 / IEC 61869-3)
CT Ratio Error (%) |  | ε_ratio = (N_actual − N_nameplate) / N_nameplate × 100 ¦ Acceptance: Class 5P: ±1%, Class 0.5: ±0.5%
CT Knee Point (Vk) |  | Vk: EMF at which 10% increase in applied V causes 50% increase in excitation current (IEC 61869-2 Cl.5.6.203)
Vk Minimum |  | Vk_min = I_fault_max × (Rct + Rburden) × ALF ¦ ALF=20 for class 5P20 ¦ Rct: CT winding resistance
Magnetising Current |  | Im = Vk / Xm ¦ At Vk: Im should be small (< 100 mA typical for class 5P CTs)
CT Phase Angle Err. |  | δ = phase displacement between primary and secondary current (in minutes of arc) ¦ Acc: ≤ 60' (class 5P)
VT Ratio Error (%) |  | ε_VT = (V_secondary_measured / V_secondary_nominal − 1) × 100 ¦ Class 0.5: ±0.5% ¦ Class 3: ±3%
VT Phase Angle |  | β = phase displacement between primary and secondary voltage ¦ Class 0.5: ≤ 20 minutes of arc
CT Polarity (DC) |  | Connect 1.5V battery to P1-P2 terminals → galvanometer on S1-S2 deflects +ve on connect, −ve on disconnect
CT Burden Check |  | Z_total_burden = R_relay + R_leads + R_CT_winding ¦ Must be ≤ CT rated burden (e.g. 3 VA = 3 Ω at 1A)
σ for CT ratio |  | σ_ratio = √[Σ(ε_i − ε̄)² / (n−1)] ¦ Multiple measurements at different primary currents ¦ Acc: σ < 0.2%
📊 STANDARD DEVIATION ANALYSIS – CT RATIO ERROR MEASUREMENTS (IEC 61869-2)
Enter ratio error % measured at 3 different primary currents (e.g. 10%, 50%, 100% of rated). Auto-calculates σ.
CT Tag | ε @ 10% (%) | ε @ 50% (%) | ε @ 100% (%) | Mean ε̄ (%) | σ (%) | Min (%) | Max (%) | Acceptance | Status
CT Ph-R (1200/1) | [7 empty] | ±1% (5P cls) | –
CT Ph-Y (1200/1) | [7 empty] | ±1% (5P cls) | –
CT Ph-B (1200/1) | [7 empty] | ±1% (5P cls) | –
CT Neutral (1200/1) | [7 empty] | ±1% (5P cls) | –
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 61869-2:2012 |  | CT: accuracy classes (5P, 10P, P), accuracy limit factor (ALF), knee point voltage definition
IEC 61869-3:2011 |  | VT: accuracy classes (0.1, 0.2, 0.5, 1, 3), phase displacement, burden, frequency response
IEC 61869-2 Cl.5.6.203 |  | Knee point voltage test: apply increasing AC voltage to CT secondary; Vk = inflection point
BS 3938:1982 |  | CT testing (historic UK standard referenced in NTDC specs): ratio, polarity, magnetisation
IEEE C57.13-2016 |  | Requirements for instrument transformers (USA equivalent of IEC 61869)
NTDC CT/VT Guideline |  | All relay-connected CT cores must be tested: ratio, polarity, knee point before commissioning
SAES-P-111 Sec.4 |  | CT accuracy: 5P20 minimum for distance relay cores. VT: class 0.5 for metering, class 3 for protection

## Trip Circuit & End-to-End
TRIP CIRCUIT SUPERVISION & END-TO-END TRIP TESTS ¦ ANSI 74 ¦ IEC 61850 ¦ 220kV A–B
Both Ends ¦ Standards: IEC 61850, IEC 60255-27, ANSI/IEEE C37.90, NTDC/WAPDA PTW & Safety Procedures
THEORY: Trip Circuit Supervision (TCS): Monitors the continuity of the trip coil circuit. An open-circuit in the trip coil path is detected and an alarm raised, preventing the CB from failing to trip. End-to-End Tests: Confirm that a relay operation at one end results in a CB trip at the correct end. PROCEDURE: (1) Apply fault at relay secondary injection terminals. (2) Verify trip contact output energised. (3) Verify CB opens (or simulated CB trip via test switch). (4) TCS: Open the trip coil circuit – verify TCS alarm raised within 2 seconds. (5) End-to-End: Coordinate with far end – inject fault and confirm both ends trip correctly. FORMULAS: Trip circuit resistance R_trip < threshold for TCS healthy state ¦ TCS alarm: open loop detected → relay raises alarm output ¦ AR sequence: CB trips → dead time → CB recloses → check stability ¦ STANDARDS: IEC 61850 (SCADA/Trip supervision), IEC 60255-27, ANSI C37.90, NTDC/WAPDA guidelines, SAES-P-111.
A. TRIP OUTPUT CONTACT VERIFICATION
Contact/Output | Function Assigned | Continuity (Ω) | Operation Confirmed (Y/N) | Contact Resistance (Ω) | Pass/Fail | Initials | Remarks
Trip Output 1 (CB Trip Coil 1) | Distance Zone Trip / OC Trip
Trip Output 2 (CB Trip Coil 2) | Backup Trip / EF Trip
Alarm Output | General Alarm / PSB Alarm
TCS Output | Trip Circuit Supervision Alarm
LED – TRIP | Trip indication on relay faceplate
LED – PICKUP | Zone pickup indication
Binary Input – Block | External block input (if used)
B. TRIP CIRCUIT SUPERVISION (TCS) TEST (ANSI 74 / IEC 61850)
Test No. | Test Description | Simulated Condition | Expected Action | Actual Action | Response Time (s) | Pass/Fail | Remarks
TCS-1 | Normal state – trip coil circuit intact | Coil loop closed | TCS healthy – no alarm
TCS-2 | Open trip coil circuit – simulate open CB | Open loop at CB | TCS alarm raised ≤ 2 s
TCS-3 | Restore trip coil circuit | Loop restored | TCS alarm clears
TCS-4 | High resistance in trip coil | Add 100 Ω series | TCS alarm / relay flags
C. END-TO-END TRIP TESTS
Test No. | Test Description | Simulated Fault | Expected Action – CKD End | Expected Action – MRD End | Actual – CKD | Actual – MRD | Pass/Fail | Remarks
E2E-1 | Zone 1 fault at CKD → Z1 trip CKD + PUTT/POTT trip MRD | Z1 fault @ CKD | Z1 Trip ≤ 35 ms | PUTT/POTT Instant Trip
E2E-2 | Zone 2 fault at CKD → Z2 timed trip CKD + PUTT trip MRD | Z2 fault @ CKD | Z2 Trip @ 350 ms | PUTT Instant Trip
E2E-3 | Phase OC fault → 51 backup trip | 3× In inject | OC Trip @ 800 ms | N/A (independent)
E2E-4 | Earth Fault → 51N backup trip | 3× Io inject | EF Trip (NI curve) | N/A
E2E-5 | Auto-Reclose sequence | Zone 1 fault | CB trips → AR → recloses | Stable or lock-out
E2E-6 | SCADA / IEC 61850 trip command | Digital trip via GOOSE | CB opens on GOOSE | Logged in SCADA
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 KEY FORMULAS – TRIP CIRCUIT & END-TO-END TESTS (IEC 61850 / ANSI 74)
TCS Supervision |  | V_TCS = V_dc − V_coil ¦ If V_TCS < threshold → TCS alarm (open coil detected) ¦ Typical TCS current ≈ 5–20 mA
Trip Coil Check |  | R_trip_coil = V_dc / I_coil ¦ Typical: 220 VDC / 0.5A = 440 Ω ¦ Measure and compare with manufacturer spec
Contact Resistance |  | R_contact ≤ 0.1 Ω (silver alloy contacts) ¦ Measure with 4-wire micro-ohmmeter at rated contact force
CB Trip Time |  | T_CB_total = T_relay_operate + T_trip_coil + T_CB_arc ¦ Total: typically 50–100 ms for 220 kV CBs
AR Dead Time |  | T_dead = time CB open → CB reclose ¦ Setting: 300ms–1s for single-phase, 500ms–3s for 3-phase AR
GOOSE Trip (IEC61850) |  | GOOSE message latency < 4 ms (IEC 61850-5 Class P2/P3) ¦ Trip via GOOSE must be confirmed at relay
End-to-End Time |  | T_end_to_end = T_relay1 + T_channel + T_relay2 + T_CB ¦ Verify against protection grading diagram
σ End-to-End |  | σ_e2e = √(σ_relay1² + σ_channel² + σ_relay2²) ¦ With independent sources: σ_total ≈ √3 × σ_relay
📋 APPLICABLE STANDARDS, DETAILS & TESTING NOTES
IEC 61850-5:2013 |  | GOOSE messaging: trip command latency class P2 (≤ 4 ms), P3 (≤ 25 ms)
IEC 60255-27:2013 |  | Trip circuit supervision: continuous monitoring, alarm on open coil within 2 seconds
ANSI/IEEE C37.90-2005 |  | Relay output contact ratings: current, voltage, burden; CB trip confirmation
IEEE C37.04-2018 |  | Rating structure for AC high-voltage circuit breakers: trip time, reclosing capability
NTDC End-to-End Policy |  | End-to-end tests mandatory at both ends before line energisation. Both CBs must confirm trip
SAES-P-111 Sec.7 |  | Trip circuit supervision: TCS relay required on all EHV CBs. AR dead time per grading study
IEC 61850-8-1:2011 |  | MMS/GOOSE protocol: trip message format, time-stamp, quality bits

## Test Summary & Defects
TEST SUMMARY, DEFECTS LOG & OVERALL RESULT ¦ 220kV A–B Line Protection
Client: NTDC ¦ Contractor: Siemens Pakistan ¦ Relays: 7SA612 + SEL-421-5 + 7SJ8021 Backup
A. TEST RESULTS SUMMARY
Sheet | Test Description | Relay | Result | PASS/FAIL | Date Tested | Initials | Defect Ref. | Closure Date | Remarks
Sh.2 | Pre-Test Checks & Insulation Resistance | Both
Sh.3 | Relay Settings Record | Both
Sh.4 | Zone 1 Reach Accuracy & Timing | Both
Sh.5 | Zone 1B (SOTF) / Zone 2 (POTT) | Both
Sh.6 | Zone 2 / Zone 4 Reach & Timing | Both
Sh.7 | Zone 3 & Zone 5 | 7SA612
Sh.8 | Directional Element | Both
Sh.9 | Power Swing / OOS Blocking | Both
Sh.10 | Load Encroachment | Both
Sh.11 | VT Fuse Failure / LOP | Both
Sh.12 | Teleprotection PUTT / POTT | Both
Sh.13 | SOTF Function | Both
Sh.14 | Backup OC/EF (7SJ8021) | 7SJ8021
Sh.15 | Fault Locator | Both
Sh.16 | CT & VT Checks | Both
Sh.17 | Trip Circuit & End-to-End | Both
OVERALL TEST RESULT: |  |  |  |  | PASS / FAIL / CONDITIONAL
B. DEFECTS LOG
Defect No. | Date Found | Description of Defect | Relay / Sheet | Severity | Action Taken | Date Closed | Closed By | Pass/Fail | Remarks
C. APPLICABLE STANDARDS REFERENCE
IEC 60255-121 |  | Distance protection relays – Performance requirements
IEC 60255-151 |  | Overcurrent protection relays – Functional requirements
IEC 60255-27 |  | General requirements for protective relays
IEC 60834-1 |  | Teleprotection equipment for EHV/HV power systems
IEC 61869-2 |  | Current transformers – Additional requirements
IEC 61869-3 |  | Voltage transformers – Additional requirements
IEC 61850 |  | Communication networks in substations (SCADA/GOOSE)
ANSI/IEEE C37.90 |  | Relays and relay systems for electric power apparatus
NTDC/WAPDA Guidelines |  | Protection relay testing & commissioning guidelines (Pakistan)
Saudi Aramco SAES-P-111 |  | Protection of high-voltage systems (Saudi Arabia)
SEC Standards |  | Saudi Electricity Company transmission protection standards
BS 3938 / BS EN 61869 |  | Current transformer specification (UK / British Standard)
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client / NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:
📐 OVERALL STATISTICAL SUMMARY – ALL TEST RESULTS
This section consolidates key measurements from all test sheets for overall project statistics. Count of PASS/FAIL results and defect density metrics per IEC 60255-121 and NTDC commissioning requirements.
KPI Metric | Total Tests | Pass | Fail | Pending | Pass Rate (%) | Defect Rate (%) | Critical Defects | Target | Status
Distance Zone Tests | 28 | [5 empty] | 0 | 100%
OC/EF Relay Tests | 16 | [5 empty] | 0 | 100%
CT/VT Tests | 12 | [5 empty] | 0 | 100%
Teleprotection Tests | 8 | [5 empty] | 0 | 100%
Pre-Test Checks | 18 | [5 empty] | 0 | 100%
Trip/End-to-End Tests | 6 | [5 empty] | 0 | 100%
OVERALL PROJECT TOTAL | 88 | [5 empty] | 0 | 100%
📐 STATISTICAL FORMULAS USED THROUGHOUT THIS PROTOCOL
Standard Deviation |  | σ = √[Σ(xi − x̄)² / (n−1)] (sample std dev, n-1 denominator for n < 30)
Mean (Average) |  | x̄ = Σxi / n ¦ EXCEL: =AVERAGE(range)
Variance |  | σ² = Σ(xi − x̄)² / (n−1) ¦ EXCEL: =VAR(range)
Coefficient of Var. |  | CoV = σ / x̄ × 100% ¦ Low CoV (<5%) = consistent measurement ¦ High CoV (>10%) = investigate
Reach Error % |  | Error% = (Measured_Reach − Set_Reach) / Set_Reach × 100 ¦ Acceptance: ¦Error%¦ ≤ 5%
Timing Tolerance |  | ΔT = max(5% × T_calculated, 30 ms) ¦ Actual trip time must be within T_calc ± ΔT
IR Temperature Corr. |  | R_ref = R_meas × 1.5^((T_ref − T_meas)/10) ¦ Reference temperature = 20°C
NI IDMT Formula |  | t = TMS × [K / ((I/Is)^α − 1)] ¦ IEC NI: K=0.14, α=0.02 ¦ IEC VI: K=13.5, α=1.0 ¦ IEC EI: K=80, α=2.0
Primary ↔ Secondary |  | Z_primary = Z_secondary / (CT_ratio / VT_ratio) = Z_sec / (1/1200)/(110/220000) = Z_sec / 0.600
Z Line Angle |  | θ = arctan(X1/R1) = arctan(0.2852/0.0311) = 83.78° (inject current lagging voltage by 83.78°)