## COVER
ABC GRID STATION – 220/132 kV
250 MVA AUTO-TRANSFORMER T-1
SECONDARY INJECTION RELAY TESTING PROTOCOLS
(Remaining Relays – Skipping A.1, A.2 & A.3)
Project |  | 220/132 kV ABC Grid Station
Client |  | ABC
Contractor |  | Siemens Pakistan Engineering Co. Ltd
Document No |  | G76001-DG101-RSPH1
Transformer Rating |  | 250 MVA, 220/132/11 kV, YNa0d1, %Z=15.57%
Document Prepared By |  | Fazli Wahid Test Inspector
Document Checked By
Date of Testing
Station Name
NG Region
RELAY TESTING INDEX – AUTO-TRANSFORMER T-1
Sheet | Relay Designation | Relay Description | CT Ratio | Status
A.4 | LV-OC | LV (132kV) Overcurrent & Earth Fault Protection | 7SJ8021 | 1600/1A | PENDING
A.5 | N-EF | Neutral Earth Fault Protection | 7SJ8021 | 1200/1A | PENDING
A.6 | TRT-OC | Tertiary Overcurrent & Earth Fault Protection | 7SJ8021 | 3000/1A | PENDING
A.7 | REF | Restricted Earth Fault Protection | 7SJ8042 | 1200/1A | PENDING
A.8 | HV-CP | HV (220kV) Connection Protection (REF) | 7SJ8041 | 1200/1A | PENDING
A.9 | LV-CP | LV (132kV) Connection Protection (REF) | 7SJ8041 | 1600/1A | PENDING
A.10 | TOL | Thermal Overload Protection | 7SJ8021 | 1600/1A | PENDING
A.11 | OVF | Over Flux (V/Hz) Protection | 7RW8020 | Via VT | PENDING
A.12 | BF-HV | Dia-4 Lower 220kV CB Breaker Failure Relay | 7VK6111 | 1200/1A | PENDING
A.13 | BF-LV | 132kV CB Breaker Failure Relay | 7VK6111 | 1600/1A | PENDING
⚠ SAFETY NOTE: All testing shall be performed with the transformer de-energised and properly earthed. Follow NTDC / WAPDA safety rules & PTW procedures. Secondary circuits must be isolated before injection.

## A.4 LV-OC
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.4 LV (132 kV) Overcurrent & Earth Fault Protection
Relay Type: | Siemens 7SJ8021-5EB90-1FA0-L05 |  |  | System Voltage: | 132 kV
CT Ratio: | 1600/1 A (Core-3) |  |  | Rated Current: | 1093.47 A (primary)
Sheet No: | 4 of 10 |  |  | Station:
Test Date: |  |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Overcurrent Pickup (IDMT) | I> = 1.44 A (secondary) = 144% × In [Primary: 2304 A]
Time Multiplier Setting (IDMT OC) | TMS = 0.135 ¦ IEC Normal Inverse (NI) Curve
Instantaneous OC | I>> = BLOCKED (no instantaneous stage)
Earth Fault Pickup (IDMT) | IEF> = 0.25 A (secondary) = 25% × In [Primary: 400 A]
TMS (Earth Fault) | TMS = 0.135 ¦ IEC Normal Inverse (NI) Curve
Instantaneous EF | IEF>> = BLOCKED
CT Ratio | 1600/1 A, Class 5P20, Burden 3 VA, Core-3 (3S1-3S4)
Relay Setting Basis | LV winding rated current = 250 MVA ÷ (√3 × 132 kV) = 1093.47 A
Operating Time (at 20× In, TMS=0.135) | ≈ 0.79 s (IEC NI formula)
B. OVERCURRENT (IDMT) INJECTION TEST – IEC Normal Inverse
Test No | Test Description | Injected Current (A sec) | Multiple of Pickup (M) | Calculated Trip Time (s) | Actual Trip Time (s) | Pass / Fail | Remarks
OC-1 | Pickup verification – Phase A | 1.44 | 1 | RELAY PICK-UP (no trip)
OC-2 | IDMT – 2× pickup (Phase A) | 2.88 | 2 | 3.11 |  |  | NI: 0.14/(M^0.02−1)×TMS
OC-3 | IDMT – 5× pickup (Phase A) | 7.2 | 5 | 1.01
OC-4 | IDMT – 10× pickup (Phase A) | 14.4 | 10 | 0.58
OC-5 | IDMT – 20× pickup (Phase A) | 28.8 | 20 | 0.43
OC-6 | Three-phase simultaneous – 5×In | 7.2 | 5 | 1.01 |  |  | Verify 3Φ trip
OC-7 | Phase B – 5× pickup | 7.2 | 5 | 1.01
OC-8 | Phase C – 5× pickup | 7.2 | 5 | 1.01
OC-9 | Reset/drop-off verification | 1.3 | ~0.9 | RELAY RESET |  |  | I< pickup×0.9
C. EARTH FAULT (IDMT) INJECTION TEST – IEC Normal Inverse
Test No | Test Description | Injected Current (A sec) | Multiple of Pickup (M) | Calculated Trip Time (s) | Actual Trip Time (s) | Pass / Fail | Remarks
EF-1 | EF Pickup verification (In circuit) | 0.25 | 1 | PICK-UP |  |  | Inject via IN terminal
EF-2 | EF IDMT – 2× pickup | 0.5 | 2 | 3.11
EF-3 | EF IDMT – 5× pickup | 1.25 | 5 | 1.01
EF-4 | EF IDMT – 10× pickup | 2.5 | 10 | 0.58
EF-5 | EF Reset verification | 0.22 | ~0.88 | RELAY RESET
D. RELAY OUTPUT & INTEGRATION CHECKS
1 | Trip output relay contacts (T1–T2) energised on phase OC trip | [5 empty] | ✓ / ✗
2 | Trip relay contacts energised on EF trip | [5 empty] | ✓ / ✗
3 | LED indicators: 'TRIP', 'PICKUP' illuminate correctly | [5 empty] | ✓ / ✗
4 | Event record shows correct fault type and trip time | [5 empty] | ✓ / ✗
5 | Binary input (BLOCK) function verified | [5 empty] | ✓ / ✗
6 | Wiring continuity to trip relay / CB confirmed | [5 empty] | ✓ / ✗
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
IEC Normal Inverse (NI): t = [0.14 / (M^0.02 − 1)] × TMS where M = I_injected / I_pickup
Example OC @ 5×: t = [0.14 / (5^0.02 − 1)] × 0.135 = [0.14/0.03270] × 0.135 ≈ 0.577 s
Primary OC pickup (A) = I_set(secondary) × CT_ratio = 1.44 × 1600 = 2304 A
Primary EF pickup (A) = I_set(secondary) × CT_ratio = 0.25 × 1600 = 400 A
Rated LV current = S / (√3 × V) = 250×10⁶ / (√3 × 132×10³) = 1093.47 A
OC setting = 144% × In_secondary = 1.44 × 1.0 A = 1.44 A (CT secondary: 1600/1A)
📝 TESTING NOTES
• All injection tests performed with secondary circuits isolated from CT secondaries.
• Tolerance on trip time: ±5% or ±30 ms (whichever is greater) per IEC 60255-151.
• Pickup current tolerance: ±5% of set value.
• Verify CT polarity and phase rotation before applying current.
• IDMT times calculated using IEC Normal Inverse formula (see formulas below).
• Blocking input must be verified to inhibit trip correctly.
• All test equipment (relay test set) calibration must be current and verified.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.5 N-EF
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.5 Neutral Earth Fault Protection
Relay Type: | Siemens 7SJ8021-5EB90-1FA0-L05 |  |  | System Voltage: | 220 kV
CT Ratio: | 1200/1 A (N BCT Core-2, 15S1-15S3) |  |  | Rated Current: | 662.69 A (HV primary)
Sheet No: | 5 of 10 |  |  | Station:
Test Date: |  |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Relay Function | Neutral (Residual) Earth Fault – Definite Time (DT)
EF Pickup Setting | I0> = 0.22 A (secondary) = 22% × In [Primary ≈ 264 A]
Operating Characteristic | IDMT Curve: DEFINITE TIME
Operating Time | t = 1.5 s (Definite Time)
CT Ratio | 1200/1 A – Neutral BCT, Core-2 (15S1-15S3)
CT Accuracy | P20, Burden 3 VA
Instantaneous Stage | NOT USED
Setting Basis | 22% × In = 0.22 × 1.0 A = 0.22 A secondary
B. DEFINITE TIME EARTH FAULT INJECTION TEST
Test No | Test Description | Injected Current (A sec) | % of Pickup | Set Trip Time (s) | Actual Trip Time (s) | Pass / Fail | Remarks
NEF-1 | Pickup verification – approach 95% then 105% | 0.21 → 0.23 | 95→105% | NO TRIP → PICK-UP |  |  | Confirm threshold
NEF-2 | Trip test – 110% pickup (0.242 A) | 0.242 | 110% | 1.5
NEF-3 | Trip test – 150% pickup (0.33 A) | 0.33 | 150% | 1.5 |  |  | DT: time constant
NEF-4 | Trip test – 200% pickup (0.44 A) | 0.44 | 200% | 1.5 |  |  | Time must be same
NEF-5 | Trip test – 500% pickup (1.10 A) | 1.1 | 500% | 1.5 |  |  | Verify DT behaviour
NEF-6 | Drop-off / reset check | 0.19 | 87% | RESET |  |  | Drop-off ≈ 0.95× pickup
NEF-7 | Polarity / phase angle check (0°) | 0.3 | 136% | 1.5 |  |  | Check phase rotation
NEF-8 | Timer accuracy verification | 0.44 | 200% | 1.5 |  |  | ±30 ms tolerance
C. OUTPUT & INTEGRATION CHECKS
1 | Trip output contacts energised on EF trip signal | [5 empty] | ✓ / ✗
2 | TRIP LED and alarm relay activated | [5 empty] | ✓ / ✗
3 | Event log records correct fault current and time | [5 empty] | ✓ / ✗
4 | Neutral CT polarity verified (Kirchhoff: sum of phase currents = neutral) | [5 empty] | ✓ / ✗
5 | Wiring continuity from N-BCT to relay and trip relay verified | [5 empty] | ✓ / ✗
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
Definite Time: operating time t = T_set (constant) = 1.50 s regardless of fault magnitude
Primary earth fault pickup = I_set(sec) × CT_ratio = 0.22 × 1200 = 264 A
Setting = 22% of In(secondary) = 0.22 × 1.0 = 0.22 A (CT: 1200/1A)
HV rated current = S / (√3 × V_HV) = 250×10⁶ / (√3 × 220×10³) = 656.08 A
N-BCT core selected: Core-2 (15S1-15S3)
📝 TESTING NOTES
• Inject current via neutral BCT secondary (1200/1 A) terminals.
• Definite Time (DT): operating time is constant regardless of fault current magnitude.
• Tolerance on trip time: ±5% or ±30 ms (whichever is greater) per IEC 60255.
• Pickup tolerance: ±5% of set value (0.22 A ± 0.011 A).
• Ensure neutral CT is not open-circuited during tests – use shorting links.
• This relay protects against HV-winding ground faults sensed via neutral CT.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.6 TRT-OC
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.6 Tertiary Overcurrent & Earth Fault Protection
Relay Type: | Siemens 7SJ8021-5EB90-1FA0-L05 |  |  | System Voltage: | 11 kV (TV winding)
CT Ratio: | 3000/1 A (Tertiary CT) |  |  | Rated Current: | 3937 A (TV primary, 75 MVA, 11 kV)
Sheet No: | 6 of 10 |  |  | Station:
Test Date: |  |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Transformer Rating – Tertiary | 75 MVA, 11 kV
TV Winding Rated Current | 75×10⁶/(√3×11×10³) = 3937 A (primary)
OC Pickup Setting | I> = 0.145 A (secondary) = 145% × In [Primary ≈ 435 A]
OC Characteristic | Definite Time (DT)
OC Operating Time | t = 1.5 s
EF Pickup Setting | IE> = 0.46 A (secondary) = 46% × In [Primary ≈ 1380 A]
EF Characteristic | Definite Time (DT)
EF Operating Time | t = 1.5 s (definite time)
CT Ratio | 3000/1 A
Setting Basis – OC | 110% × In: 3937×1.10/3000 = 0.144 A ≈ 0.145 A
Setting Basis – EF | 35% × In: 3937×0.35/3000 = 0.459 A ≈ 0.46 A
B. OVERCURRENT (DT) INJECTION TEST
Test No | Test Description | Injected Current (A sec) | % of Pickup | Set Trip Time (s) | Actual Trip Time (s) | Pass / Fail | Remarks
OC-1 | Pickup – 95% → 105% | 0.138→0.152 | 95→105% | NO TRIP→PICKUP
OC-2 | Trip at 150% pickup (0.22 A) | 0.218 | 150% | 1.5
OC-3 | Trip at 200% (0.29 A) | 0.29 | 200% | 1.5 |  |  | DT constant
OC-4 | Trip at 500% (0.73 A) | 0.725 | 500% | 1.5
OC-5 | Phase B – 150% pickup | 0.218 | 150% | 1.5
OC-6 | Phase C – 150% pickup | 0.218 | 150% | 1.5
OC-7 | Reset verification | 0.13 | ~90% | RESET |  |  | Drop-off ratio
C. EARTH FAULT (DT) INJECTION TEST
Test No | Test Description | Injected Current (A sec) | % of Pickup | Set Trip Time (s) | Actual Trip Time (s) | Pass / Fail | Remarks
EF-1 | EF Pickup – 95% → 105% | 0.437→0.483 | 95→105% | NO TRIP→PICKUP |  |  | Inject via IN terminal
EF-2 | EF trip at 150% (0.69 A) | 0.69 | 150% | 1.5
EF-3 | EF trip at 200% (0.92 A) | 0.92 | 200% | 1.5
EF-4 | EF Reset | 0.43 | ~93% | RESET
D. OUTPUT & INTEGRATION CHECKS
1 | OC trip contacts energised on phase OC trip | [5 empty] | ✓ / ✗
2 | EF trip contacts energised on earth fault trip | [5 empty] | ✓ / ✗
3 | TRIP and PICKUP LEDs operational | [5 empty] | ✓ / ✗
4 | Event log records fault current & type | [5 empty] | ✓ / ✗
5 | Blocking input verified | [5 empty] | ✓ / ✗
6 | Wiring to tertiary winding CT and trip relay confirmed | [5 empty] | ✓ / ✗
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
TV rated current = S_TV / (√3 × V_TV) = 75×10⁶ / (√3 × 11×10³) = 3937 A (primary)
OC secondary pickup = (110% × 3937) / 3000 = 4330.7/3000 = 0.1443 A ≈ 0.145 A
EF secondary pickup = (35% × 3937) / 3000 = 1377.95/3000 = 0.459 A ≈ 0.46 A
Primary OC trip level = 0.145 × 3000 = 435 A
Primary EF trip level = 0.46 × 3000 = 1380 A
📝 TESTING NOTES
• Tertiary winding rated: 75 MVA, 11 kV delta winding.
• Inject via CT secondary (3000/1 A) terminals for all tests.
• Definite Time: trip time is constant regardless of current magnitude.
• Tolerance: ±5% on pickup current, ±30 ms on trip time.
• Verify both OC and EF functions trip separate outputs if applicable.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.7 REF
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.7 Restricted Earth Fault (REF) Protection
Relay Type: | Siemens 7SJ8042-5EB90-1F80-L05 |  | System Voltage: | 220/132 kV
CT Ratio: | HV BCT 1200/1A ¦ LV BCT 2400/1A ¦ N BCT 1200/1A |  | Rated Current: | 1093.47 A (LV) / 656.08 A (HV)
Sheet No: | 7 of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Type | High-Impedance Restricted Earth Fault (REF)
CT Cores | HV BCT Core-3 (3S1-3S2) ¦ LV BCT Core-2 (8S1-8S2) ¦ N BCT Core-2 (14S1-14S2)
CT Ratio Selected | 1200/1 A (top: 2400:1200/1-1A)
CT Class / Burden | P20, 3 VA
CT Knee Point Voltage (Vk) | ≥ 400 V (as per bushing CT data)
CT Magnetising Current (Ie at Vk) | 0.15 A
CT Secondary Winding Resistance (Rct) | 5 Ω (max, HV); 12 Ω (LV BCT)
Lead Resistance (Rl) | 0.758 Ω (250m, 6mm², at 75°C = 0.884 Ω)
Min. Setting Voltage Vs (calculated) | Vs ≥ 43.35 V → Set Vs = 100 V
Relay Setting Current (Is) | Is = 0.07 A (Address 2706: 0.07 A)
Primary Operating Current | ≈ 218.7 A
Stabilising Resistor (Rs) | 990 Ω (variable, 0–1500 Ω)
Metrosil Required | YES – external non-linear resistor required (peak V > 2kV)
CT Dimensioning Check | Vk ≥ 2 × Vs → 400 ≥ 200 V ✓ SATISFIED
B. HIGH-IMPEDANCE REF INJECTION TEST PROCEDURE
Step | Test | Procedure | Pass Criterion |  | Measured Value | Pass/Fail
STEP 1 | CT Magnetising Curve Check | Apply voltage across each CT secondary winding. Measure magnetising current at Vs=100V. Record and compare with manufacturer data (Ie_at_Vs ≤ 0.02A expected). | Ie @ Vs = 100V ≤ 0.02 A |  |  | ✓
STEP 2 | Stability Test (through-fault) | Inject full rated current (In) through CTs connected in parallel (through fault condition). Relay must NOT operate. Test for 10 seconds. | NO TRIP for I < Is |  |  | ✓
STEP 3 | Operate Test – Internal Fault Simulation | Inject current into the relay circuit (differential current). Increase until relay picks up. Record operating current. | Is = 0.07 A (sec) |  | Measured: ____ A | ✓
STEP 4 | Trip Time – Operate Condition | Inject 2× Is (0.14 A) and measure trip time. REF operates in definite time. | < 40 ms (instantaneous) |  | Measured: ____ ms | ✓
STEP 5 | Stabilising Resistor Verification | Measure resistance of Rs across relay terminals. Verify = 990 Ω ± 5%. | 990 Ω ± 50 Ω |  | Measured: ____ Ω | ✓
STEP 6 | Metrosil Verification | Confirm Metrosil non-linear resistor is installed across relay terminals. Apply Vm_peak < 2kV transient – resistor must clamp voltage. | Metrosil Present: YES |  |  | ✓
STEP 7 | Sensitivity Check | Confirm primary operating current = N × (n_CT × Is + n×Ie) ≈ 218.7 A. This is 218.7/1093.47 = 20.0% of full load. | Primary I_operate ≈ 219 A |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
Minimum setting voltage: Vs_min = I_through_fault_max × (Rct + 2×Rl) / N
= 702291 × (5 + 2×0.884) / 1200 = 43.35 V → Set 100 V
Stabilising resistor: Rs = Vs / Is − Rrelay = 100/0.07 − 5 ≈ 1424 Ω (set 990 Ω per doc)
Primary operating current: Iop = N × [Is + n×Ie_at_Vs]
= 1200 × [0.07 + 3×0.0000260] = 84.09 A × (N/n) factor → 218.7 A
CT dimensioning check: Vk ≥ 2 × Vs → 400 ≥ 200 ✓
Metrosil required if: V_peak > 2 kV (V_peak = √2 × √[2×Vk×(Vmax_fault − Vk)])
📝 TESTING NOTES
• This is a HIGH-IMPEDANCE differential REF scheme – DO NOT inject voltage >Vk into CTs.
• All three CTs (HV, LV, Neutral) must be connected in circulating current configuration.
• Metrosil and stabilising resistor must be in circuit for all stability and trip tests.
• If Vk of any CT is insufficient (< 2Vs), that CT must be replaced before commissioning.
• Primary operating current ≈ 219 A = 20% of LV full-load current (sensitivity is good).
• Isolated testing of relay is acceptable for pickup and time measurement.
• Primary CT polarity (star-point direction) must face protected object.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:

## A.8 HV-CP
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.8 HV (220 kV) Connection Protection (High-Z REF)
Relay Type: | Siemens 7SJ8041-5EB90-1F80-L05 |  | System Voltage: | 220 kV
CT Ratio: | HV Bushing CT: 2400/1200/1-1A ¦ HV Lower/Mid CT: 2400/1200/1-1A |  | Rated Current: | 656.08 A (HV, 220kV)
Sheet No: | 8 of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Type | High-Impedance Restricted Earth Fault – HV (220kV) Connection
HV Bushing CT | Core-1: 181-182, Ratio 2400:1200/1-1A, Class P20, Burden 3VA
HV Lower/Mid CT | Core-2: 251-253, Ratio 2400:1200/1-1A, Class 5P20, Burden 0VA
CT Ratio (selected) | 1200/1 A (secondary: 1 A)
CT Knee Point Voltage | ≥ 2600 V (per nameplate)
CT Magnetising Current (Ie @ Vk) | 0.02 A
CT Rct | 12 Ω (HV Mid CT)
Lead Resistance (Rl @ 75°C) | 0.884 Ω
Min. Setting Voltage (Vs calc.) | 43.35 V → Set Vs = 100 V (Address 2706)
Relay Setting Current (Is) | Is = 0.37 A (Address 2706: 0.37 A)
Primary Operating Current | ≈ 217.8 A (≈ 33% of rated HV current)
Stabilising Resistor (Rs) | 200 Ω (calculated ≈ 265 Ω, set 200 Ω per doc)
No. of CT cores (n) | 3
Metrosil Required | YES (peak voltage > 2 kV)
Continuous Rs Power Rating | 8 W ¦ Short-time: 5086 W
CT Dimensioning Check | Vk (2600V) ≥ 2 × Vs (200V) ✓ SATISFIED (ratio: 13×)
B. HIGH-IMPEDANCE HV CONNECTION PROTECTION – TEST PROCEDURE
Step | Test | Procedure | Pass Criterion |  | Measured | Pass/Fail
STEP 1 | CT Mag. Check | Measure magnetising current of each CT at Vs=100V. All cores must meet Ie ≤ 0.02 A. | Ie ≤ 0.02 A @ 100V |  |  | ✓
STEP 2 | Through-fault Stability | Inject maximum through-fault current (4214 A primary / 3.51 A secondary) in all CT secondaries in parallel. Verify relay does NOT operate. | No operation |  |  | ✓
STEP 3 | Pickup Test | Inject differential (spill) current into relay circuit, gradually increasing from 0. Record current at which relay picks up. | Is = 0.37 A |  | Meas: ___A | ✓
STEP 4 | Instantaneous Trip Time | Inject 2× Is into relay circuit. Measure trip time. | < 40 ms |  | Meas: ___ms | ✓
STEP 5 | Stabilising Resistor Check | Measure Rs across relay terminals with ohmmeter (circuit de-energised). | 200 Ω ± 10 Ω |  | Meas: ___Ω | ✓
STEP 6 | Metrosil Verification | Confirm Metrosil installed; verify clamps transient voltage under internal fault. | Installed: YES |  |  | ✓
STEP 7 | Sensitivity Confirm | Primary operating current = N × Is = 1200 × 0.37 ≈ 444 A (includes CT mag current → 217.8 A per calc). | Iop ≈ 218 A |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
Max. through-fault current (ext.) = S / (√3 × V × %Z) = 250×10⁶/(√3×220×10³×0.1557) = 4213.74 A
Vs_min = I_through × (Rct + 2Rl) / N = 4213.74 × (12+2×0.884)/1200 = 48.8 V → set 100 V
Rs_calc = Vs/Is − Rrelay = 100/0.37 − 5 = 265.3 Ω (set 200 Ω per approved doc)
Continuous Rs power = Vs² / Rs = 100² / 200 = 50 W (check: doc shows 8W → Is×Vs = 0.37×100 = 37W)
Metrosil required: V_peak = √2×√[2×Vk×(Vmax−Vk)] check exceeds 2 kV
📝 TESTING NOTES
• HV Connection Protection covers the zone between HV bushing CTs and HV lower/mid CTs.
• High-impedance scheme: relay voltage across its terminal is the sensitive parameter.
• Both HV Bushing CT (Core-1) and HV Lower CT (Core-2) must be used.
• Vs = 100V is set to ensure security against external faults with CT saturation.
• RMS voltage across Rs during internal fault = 13.4 V → Rs continuous power = 8 W.
• Short-time power across Rs = 5086 W – ensure Rs can handle this (thermal rating).
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:

## A.9 LV-CP
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.9 LV (132 kV) Connection Protection (High-Z REF)
Relay Type: | Siemens 7SJ8041-5EB90-1F80-L05 |  | System Voltage: | 132 kV
CT Ratio: | LV Bushing CT: 2000/1A ¦ 132kV CT: 1600:800:400/1-1-1A |  | Rated Current: | 1093.47 A (LV, 132kV)
Sheet No: | 9 of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Type | High-Impedance Restricted Earth Fault – LV (132kV) Connection
LV Bushing CT | Core-4: 1051-1052, CT Ratio 2000/1A
132kV CT | Core-2: 251-254, Ratio 1600:800:400/1-1-1A, Class 10P20
CT Ratio Selected | 1600/1 A (secondary: 1 A)
CT Knee Point Voltage (Vk) | 60,000 V (nameplate) – far exceeds minimum
CT Magnetising Current (Ie @ Vk) | 0.15 A
CT Rct | 7.8 Ω
Lead Resistance (Rl @ 75°C) | 0.884 Ω
Min. Setting Voltage (Vs calc.) | 42.0 V → Set Vs = 100 V
Relay Setting Current (Is) | Is = 0.83 A (Address 2706: 0.83 A)
Primary Operating Current | ≈ 256 A (23.4% of rated LV current)
Stabilising Resistor (Rs) | Set per calculation (≈120 Ω; doc: see approved setting)
No. of CT cores (n) | 3
Metrosil Required | YES
CT Dimensioning Check | Vk (60,000V) >> 2×Vs (200V) ✓ SATISFIED
B. LV CONNECTION PROTECTION – TEST PROCEDURE
Step | Test | Procedure | Pass Criterion |  | Measured | Pass/Fail
STEP 1 | CT Mag. Curve Check | Measure Ie at Vs=100V for each of the 3 CT cores. Record and verify within limits. | Ie ≤ 0.02 A @ 100V |  | Meas: ___A | ✓
STEP 2 | Through-fault Stability | Inject maximum through-fault current (7022.9 A primary / 4.39 A secondary at 1600:1). All CTs in parallel; relay must NOT operate. | No operation |  |  | ✓
STEP 3 | Pickup Test | Inject differential current into relay circuit. Increase until relay picks up. Record operating current. | Is = 0.83 A |  | Meas: ___A | ✓
STEP 4 | Instantaneous Trip | Inject 2× Is (1.66 A) into relay. Measure trip time. | < 40 ms |  | Meas: ___ms | ✓
STEP 5 | Stabilising Resistor | Measure Rs in relay circuit (de-energised). Confirm set value. | As per approved doc |  | Meas: ___Ω | ✓
STEP 6 | Metrosil Check | Confirm Metrosil installed. Check voltage clamping under internal fault condition. | Installed: YES |  |  | ✓
STEP 7 | Sensitivity | Primary operating current = N × Is = 1600 × 0.0565 × factor ≈ 256 A = 23.4% of In. | Iop ≈ 256 A |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
Max. through-fault current (LV) = S/(√3×V×%Z) = 250×10⁶/(√3×132×10³×0.1557) = 7022.9 A
Vs_min = I_ext_max × (Rct + 2Rl) / N = 7022.9 × (7.8 + 2×0.884) / 1600 = 42.0 V
Setting Vs = 100 V gives safety margin of 100/42 = 2.38 (adequate)
Rs_calc = Vs/Is − Rrelay = 100/0.83 − 5 ≈ 115.5 Ω
Primary operating current = N × (Is + n×Ie) = 1600 × (0.0565 + 3×0.02) = 186.4 A → 256 A per doc
📝 TESTING NOTES
• LV Connection Protection covers the zone between LV Bushing CT and 132kV CT.
• High-Impedance scheme: stability ensured by setting Vs > Vs_min.
• CT knee-point (60kV) far exceeds requirement – excellent stability margin.
• Metrosil must be installed and checked before energisation.
• Primary sensitivity = 256 A = 23.4% of 1093.47 A rated LV current.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:

## A.10 TOL
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.10 Thermal Overload Protection
Relay Type: | Siemens 7SJ8021-5EB90-1FA0-L05 |  | System Voltage: | 132 kV
CT Ratio: | 1600/1 A (LV CT) |  | Rated Current: | 1093.47 A (rated, LV)
Sheet No: | 10 (a) of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Function | Thermal Overload Protection with memory (IEC 60255-149 / IEC 60076-2)
Transformer Rating | 250 MVA, 132 kV (LV side monitored)
Rated Current (In) | 1093.47 A (primary) ¦ 0.683 A (secondary, 1600/1A CT)
Max. Preload Current (Ipre) | 1093.5 A (primary) ¦ 0.684 A (secondary)
k-Factor Setting | k = Imax / Ipre = 1476/1093.5 = 1.35 (permissible: 135% of In)
Thermal Time Constant (τ) | τ = 90 minutes (set per transformer thermal withstand)
Alarm Stage (θ_alarm / θ_trip) | 95% (alarm at 95% of trip temperature)
Operating Characteristic | Thermal image model: τ × dθ/dt + θ = k² × I²
CT Ratio | 1600/1 A
Relay Address Settings | FCT 49 = ON ¦ k = 1.35 ¦ τ = 90 min ¦ θ_alarm = 95%
B. THERMAL OVERLOAD – INJECTION TEST PROCEDURE
Test No | Test Description | Procedure | Pass Criterion |  | Measured | Pass/Fail
TOL-1 | Function Enable Check | Verify FCT 49 = ON in relay menu. Check thermal image display shows 0% on cold start. | FCT 49 = ON, θ = 0% |  |  | ✓
TOL-2 | Alarm Stage Test (Cold) | Inject 1.35 × In (secondary = 0.92 A) continuously. Monitor relay display. Alarm must appear at 95% thermal state. Note alarm time. | Alarm @ θ = 95% |  | Meas. time: ___min | ✓
TOL-3 | Trip Test (Cold) | Continue injecting 1.35 × In until thermal trip at θ = 100%. Record time from start to trip. | Trip @ θ = 100% |  | Trip time: ___min | ✓
TOL-4 | Thermal Memory Test (Hot Start) | After TOL-3, allow partial cool-down (< τ). Re-inject. Relay should trip faster due to retained thermal image. | Trip faster than TOL-3 |  |  | ✓
TOL-5 | Overload at 120% In | Inject 1.20 × In (1.2 × 0.683 = 0.82 A). Verify relay starts accumulating thermal image. No immediate trip. | θ increasing, no immediate trip |  |  | ✓
TOL-6 | k-factor Verification | Inject exactly k×In (= 1.35 × 0.683 = 0.922 A). Monitor: relay must reach thermal equilibrium at 100%. | Thermal equilibrium @ θ=100% |  |  | ✓
TOL-7 | Cold Reset Check | After full cooldown (several × τ), verify thermal image resets to 0%. | θ = 0% after cooldown |  |  | ✓
TOL-8 | Alarm Output Contact | Verify alarm output relay energises at θ = 95%. | Alarm contact closed @ 95% |  |  | ✓
TOL-9 | Trip Output Contact | Verify trip output relay energises at θ = 100%. | Trip contact closed @ 100% |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
Thermal model: τ × dθ/dt + θ = (I/k×In)² — steady state: θ_ss = (I/k×In)²
Trip condition: θ = 1.00 (100%) → I_trip = k × In (continuous)
Alarm: θ_alarm = 0.95 (95%) → set value: 95%
k = I_max_continuous / I_rated = 1476 A / 1093.47 A = 1.3497 ≈ 1.35
Secondary test current = k × In(sec) = 1.35 × (1093.47/1600) = 1.35 × 0.683 = 0.922 A
Thermal time for cold start to trip at k×In: t_trip = τ × ln[(k²)/(k²−1)] = 90×ln(1.35²/(1.35²−1))
📝 TESTING NOTES
• Thermal model includes a memory function – thermal state is NOT reset on relay power cycle.
• Time constant τ = 90 min represents the transformer's thermal time constant.
• k = 1.35 means transformer can sustain 135% of rated current continuously without damage.
• Alarm at 95% gives operator ~5% headroom to take corrective action before trip.
• Full thermal tests may take several hours – plan accordingly.
• This relay uses LV CT (1600/1A) as it monitors LV winding thermal condition.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:

## A.11 OVF
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.11 Over Flux (V/f) Protection
Relay Type: | Siemens 7RW8020-5EB90-1DD0-L05 |  |  | System Voltage: | 220/132 kV
CT Ratio: | Via VT (secondary: 100V/√3 per phase) |  |  | Rated Current: | Voltage-based (V/f ratio)
Sheet No: | 10 (b) of 10 |  |  | Station:
Test Date: |  |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Function | Over-excitation (Volts/Hertz) Protection – ANSI 24
Standard Reference | IEC 60076-1 / IEEE C37.106 / Siemens 7RW80 Manual
Rated System Frequency | 50 Hz
Rated VT Secondary Voltage | 6 kV (phase-to-phase) → per relay configuration
Min. Trip Command Duration | 0.15 s
Warning Stage (U/f >) | 1.05 pu ¦ Delay = 10 s (alarm only)
Definite Time Stage (U/f >>) | 1.10 pu ¦ Fast definite-time trip
Stepped Characteristic | Enabled – see time-voltage table below
Cooldown Timer | 900 s (15 minutes) after thermal trip
Over-excitation Protection | FCT = ON (U/f mode active)
B. V/f CHARACTERISTIC – APPROVED OPERATING TIMES
The following stepped characteristic defines the maximum permissible overflux duration vs magnitude. Times are programmed into relay addresses 4306–4313.
Address | V/f Level (pu) | % of Nominal | Set Trip Time (s) | Injected V/f | Actual Trip Time (s) | Pass/Fail | Remarks
4306 | 1.05 | 105% | See approved doc |  |  |  | Warning stage – alarm output
4307 | 1.1 | 110% | See approved doc
4308 | 1.15 | 115% | See approved doc
4309 | 1.2 | 120% | See approved doc
4310 | 1.25 | 125% | See approved doc
4311 | 1.3 | 130% | See approved doc
4312 | 1.35 | 135% | See approved doc
4313 | 1.4 | 140% | See approved doc |  |  |  | Fastest stage
C. OVER FLUX TEST PROCEDURE
Test No | Test Description | Procedure |  | Pass Criterion |  | Measured | Pass/Fail
OVF-1 | Warning Stage Test | Apply VT secondary voltage = 1.05 × Vn at 50 Hz. Verify alarm (warning) output after 10s delay. |  | Alarm after 10 s |  | Meas: ___s | ✓
OVF-2 | Definite Time Trip Stage (U/f>>) | Apply voltage = 1.10 × Vn at 50 Hz. Verify trip output within set definite time. |  | Trip per approved time |  | Meas: ___s | ✓
OVF-3 | Reduced Frequency Test | Apply rated voltage at reduced frequency (e.g. 47 Hz). V/f = Vn/47×50 = 1.064 pu. Verify relay picks up warning. |  | V/f > 1.05 → alarm |  |  | ✓
OVF-4 | Characteristic Verification at 1.20 pu | Apply 1.20 × Vn at 50 Hz. Verify trip within time at address 4309. |  | Per 4309 setting |  | Meas: ___s | ✓
OVF-5 | Characteristic Verification at 1.40 pu | Apply 1.40 × Vn at 50 Hz. Verify fastest trip time (address 4313). |  | Per 4313 setting |  | Meas: ___s | ✓
OVF-6 | Cooldown Timer Check | After trip, verify cooldown timer of 900 s before auto-reclosure allowed. |  | 900 s cooldown |  |  | ✓
OVF-7 | Normal Condition – No Trip | Apply exactly 1.00 × Vn at 50 Hz (V/f = 1.00). Relay must NOT operate. |  | No trip, no alarm |  |  | ✓
OVF-8 | Alarm Output Contact | Verify alarm relay contact closes at warning stage. |  | Contact closed @ 1.05 pu |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
V/f ratio (pu) = V_applied(pu) / f_applied(pu) = [V/Vn] / [f/fn]
Example: V=110%Vn, f=50Hz → V/f = 1.10/1.0 = 1.10 pu (exceeds warning)
Example: V=100%Vn, f=47Hz → V/f = 1.0/0.94 = 1.064 pu (exceeds 1.05 warning)
Flux density B ∝ V / (f × N × A) where N=turns, A=core area
Over-excitation leads to: core loss increase, winding overheating, insulation stress
📝 TESTING NOTES
• Over-excitation occurs when V/f ratio exceeds transformer iron core design limits.
• Typical limit: B ∝ V/f; exceeding rated flux damages insulation and core laminations.
• The 7RW80 relay uses VT input only – no CT measurement required.
• Relay is set to VT secondary of 6kV (per approved setting doc). Verify VT ratio and connections.
• Stepped characteristic provides better transformer protection than simple definite-time.
• Cooling down period of 900s ensures transformer core de-magnetizes before re-energisation.
• The 5th harmonic blocking (40%) is set in the differential relay (A.1/A.2), not this relay.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.12 BF-HV
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.12 Dia-4 Lower 220 kV CB Breaker Failure Relay
Relay Type: | Siemens 7VK6111-5AB92-4YC0-L05 |  | System Voltage: | 220 kV
CT Ratio: | 1200/1 A |  | Rated Current: | 656.08 A (HV rated)
Sheet No: | 10 (c) of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Function | Circuit Breaker Failure Protection (CBFP) – ANSI 50BF
System Voltage | 220 kV
3-ph Fault Level (CB SC Rating) | 40 kA (Switchgear rating)
CT Ratio | 1200/1 A
Relay Current Rating | 1 A (secondary)
Current Pick-up Setting | I_BF = 0.1 × In = 0.1 A (secondary) [Primary = 120 A]
Setting Range (current) | 0.05 × In – 20.0 × In
T1 – Local CB Re-trip Delay | T1 = 0.1 s (3-pole re-trip to local feeder CB)
T2 – Adjacent CB Trip Delay | T2 = 0.25 s (2nd stage: adjacent bus CB trip)
Local Defective CB → Adjacent Trip | 0.25 s (same as T2)
T2 Start Criteria | Parallel with T1 (T2 starts simultaneously with T1)
Trip Output – Defective CB | Trip with T2 signal (trips adjacent bus-section breakers)
CB Auxiliary Contact Monitoring | YES – CB 52a/52b contacts monitored
Scheme | Re-trip local CB first (T1), then adjacent breakers (T2)
B. BREAKER FAILURE RELAY – TEST PROCEDURE
Test No | Test Description | Procedure | Pass Criterion |  | Measured | Pass/Fail
BF-1 | Current Pickup Verification | Inject single-phase AC current, ramp up from 0. Record current at which BF current detector picks up. | I_pickup = 0.10 A ±5% secondary |  | Meas: ___ A | ✓
BF-2 | Current Drop-off / Reset | With BF started, reduce current below pickup. Record drop-off current (≈0.95 × pickup). | Drop-off ≈ 0.095 A |  | Meas: ___ A | ✓
BF-3 | T1 Timer Test – Local Re-trip | Initiate BF start signal (simulate protection trip). Maintain current above I_BF. Measure time to T1 output (local CB re-trip). | T1 = 0.100 s ±30ms |  | Meas: ___ ms | ✓
BF-4 | T2 Timer Test – Adjacent CB Trip | Continue from BF-3 (or restart). Measure time from BF start to T2 output. | T2 = 0.250 s ±30ms |  | Meas: ___ ms | ✓
BF-5 | CB Auxiliary Contact Check | Open 52b contact (CB open indication) while fault current flowing. Verify BF logic resets (CB has operated correctly). | BF resets when 52b opens |  |  | ✓
BF-6 | No-current Reset | Apply BF start, then remove fault current within T1 window. BF must reset (CB operated – current dropped). | BF resets without T2 output |  |  | ✓
BF-7 | BF Start Input Test | Apply BF_START binary input from protection relay. Verify BF logic initiates correctly. | BF logic starts on BF_START |  |  | ✓
BF-8 | Output Contact Verification | Verify T1 and T2 output contacts are wired to correct trip circuits and operate. | T1 → local CB, T2 → adjacent CBs |  |  | ✓
BF-9 | Three-phase Symmetry | Repeat current pickup test for phase B and phase C. | I_pickup ≈ 0.10 A for all 3 phases |  |  | ✓
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NTDC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
BF current pickup (primary) = I_set(sec) × CT_ratio = 0.10 × 1200 = 120 A
T_BF_total = T1 + CB_opening_time → T2 must be > T1 + CB_opening time (typ. 3-5 cycles)
At 50 Hz: 1 cycle = 20ms, 3 cycles = 60ms → T2 = 250ms provides 150ms margin
BF sensitivity = 0.1×In = 10% of rated current → detects even resistive fault CB failures
📝 TESTING NOTES
• BFR initiates when: protection trip issued AND CB current still flowing after T1 delay.
• T1 = 0.1s: re-trips the local 220kV CB (gives CB a second chance to open).
• T2 = 0.25s: trips all adjacent CBs connected to same bus section.
• CB failure is detected by current still flowing despite trip command being issued.
• CB 52a/52b contacts provide confirmation of CB position for logic supervision.
• Low set current detector (0.1 × In = 0.1 A sec = 120 A primary) provides high sensitivity.
• IEC 60255-26 and IEC 61850 RBRF functional block standard applies.
• Verify BF_START input wiring from all protection relays (A.1–A.11) that can initiate BF.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date:

## A.13 BF-LV
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 RELAY TESTING PROTOCOL
A.13 132 kV CB Breaker Failure Relay
Relay Type: | Siemens 7VK6111-5AB12-4TC0-L05 |  | System Voltage: | 132 kV
CT Ratio: | 1600/1 A |  | Rated Current: | 1093.47 A (LV rated)
Sheet No: | 10 (d) of 10 |  | Station:
Test Date: |  |  | Tested By:
A. PRE-TEST INFORMATION & RELAY SETTINGS
Protection Function | Circuit Breaker Failure Protection (CBFP) – ANSI 50BF
System Voltage | 132 kV
3-ph Fault Level (CB SC Rating) | 40 kA (Switchgear rating)
CT Ratio | 1600/1 A
Relay Current Rating | 1 A (secondary)
Current Pick-up Setting | I_BF = 0.1 × In = 0.1 A (secondary) [Primary = 160 A]
Setting Range (current) | 0.05 × In – 20.0 × In
T1 – Local CB Re-trip Delay | T1 = 0.225 s (3-pole re-trip to local 132kV feeder CB)
T2 – Adjacent CB Trip Delay | T2 = 0.250 s (2nd stage: adjacent bus section CBs)
Local Defective CB → Adjacent Trip | T = 0.225 s → 0.250 s
T2 Start Criteria | Parallel with T1
Gnd Zone Protection | Ground zone bus-bar protection also starts BFR
Trip Output – Defective CB | Trip with T2 signal
CB Auxiliary Contact Monitoring | YES
Scheme | Re-trip local 132kV CB (T1), then adjacent 132kV bus CBs (T2)
B. 132kV BFR – TEST PROCEDURE
Test No | Test Description | Procedure | Pass Criterion |  | Measured | Pass/Fail
BF-1 | Current Pickup – Phase A | Inject single-phase AC, ramp from 0. Record pickup current. | I = 0.10 A ±5% sec |  | Meas: ___ A | ✓
BF-2 | Current Pickup – Phase B & C | Repeat pickup test for phases B and C. | I = 0.10 A ±5% each phase |  | Meas: ___ A | ✓
BF-3 | Drop-off Verification | Reduce current from above pickup to below. Record drop-off level. | Drop-off ≈ 0.095 A |  | Meas: ___ A | ✓
BF-4 | T1 Timer – Local Re-trip | Apply BF start + fault current > I_BF. Measure time to T1 output. | T1 = 225 ms ±30ms |  | Meas: ___ ms | ✓
BF-5 | T2 Timer – Adjacent Bus Trip | Apply BF start + fault current > I_BF. Measure time to T2 output. | T2 = 250 ms ±30ms |  | Meas: ___ ms | ✓
BF-6 | CB Auxiliary Contact Supervision | Open 52b during test (CB operated correctly). Verify BF logic resets before T2. | BF resets, T2 not issued |  |  | ✓
BF-7 | Ground Zone Start Input | Apply BF start from ground zone bus protection input. Verify BF initiates. | BF starts on Gnd Zone input |  |  | ✓
BF-8 | No-current Trip Reset | BF start input applied, but current removed before T1. BF must reset. | No T1 or T2 output |  |  | ✓
BF-9 | T1 Output Contact | Verify T1 output contact wired to local 132kV CB trip coil. | Contact closed @ T1 |  |  | ✓
BF-10 | T2 Output Contact | Verify T2 contact wired to adjacent 132kV bus-section CBs. | Contact closed @ T2 |  |  | ✓
C. HV vs LV BFR COMPARISON TABLE
Parameter |  | A.12 – HV 220kV BFR |  | A.13 – LV 132kV BFR
Relay Type |  | 7VK6111-5AB92-4YC0 |  | 7VK6111-5AB12-4TC0
CT Ratio |  | 1200/1 A |  | 1600/1 A
Current Pickup (sec) |  | 0.10 A (0.1×In) |  | 0.10 A (0.1×In)
Primary Pickup (A) |  | 120 A |  | 160 A
T1 – Re-trip Delay |  | 0.100 s |  | 0.225 s
T2 – Adjacent Trip |  | 0.250 s |  | 0.250 s
System Voltage |  | 220 kV |  | 132 kV
📋 NOTES, REFERENCES & STANDARDS
▪ IEC 60255 series – Measuring relays and protection equipment
▪ IEC 60076 – Power Transformers
▪ BS 142 – Electrical Protection Relays
▪ NGC/WAPDA Protection Relay Testing Guidelines
▪ ANSI/IEEE C37.90 – Relays and Relay Systems Associated with Electric Power Apparatus
▪ Siemens 7SJ80/7SJ81 Relay Manual (relay-specific)
📐 KEY FORMULAS USED
BF current pickup (primary) = I_set(sec) × CT_ratio = 0.10 × 1600 = 160 A
Total fault clearing time = Protection operate time + T2 + CB_opening_time of adjacent CB
At 50 Hz: T1=225ms=11.25 cycles, T2=250ms=12.5 cycles (adequate for 132kV CB operation)
T1 must be > CB_fault_clearing_time (typ. 3–5 cycles = 60–100ms at 50Hz) for 132kV
BF sensitivity = 0.1 × 1600 = 160 A = 14.6% of rated LV current (1093 A)
📝 TESTING NOTES
• 132kV BFR T1 = 0.225s (longer than HV 0.1s) – allows for 132kV CB operating time characteristics.
• T2 = 0.250s for both HV and LV BFRs – consistent inter-stage coordination.
• Ground zone bus protection input initiates the 132kV BFR in addition to object protections.
• Verify all BF start inputs from: Differential (A.1/A.2), LV-OC (A.4), REF (A.7), LV-CP (A.9) relays.
• Current pickup 0.1×In is very sensitive – detects even high-resistance CB failure conditions.
• Testing per IEC 62271 (HV switchgear) and IEC 60255-26 relay testing standards.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) | WITNESSED BY (Client Rep.) |  | APPROVED BY (Project Manager)
Name: |  | Name: | Name: |  | Name:
Designation: |  | Designation: | Designation: |  | Designation:
Signature: |  | Signature: | Signature: |  | Signature:
Date: |  | Date: | Date: |  | Date: