## COVER
ABC GRID STATION – 220/132 kV
250 MVA AUTO-TRANSFORMER T-1
COMPREHENSIVE RELAY TESTING PROTOCOLS
Relays A.1 (Diff Set-1) ¦ A.2 (Diff Set-2) ¦ A.3 (HV OC & EF)
Project Name |  |  | ABC 220kV Substation – 250 MVA Auto-Transformer T-1 Protection
Client / Witness |  |  | ABC
Contractor |  |  | Siemens Pakistan Engineering Co. Ltd
Document No |  |  | G76001-DG101-RSPH1
Transformer Rating |  |  | 250 MVA, 220/132/11 kV, YNa0d1, %Z=15.57%, OLTC ±10%, 33 taps
Vector Group |  |  | YNa0d1 (HV=YN, LV=Auto a0, TV=delta d1)
Test Method |  |  | Secondary Injection (offline, transformer de-energised)
Date of Testing
Ambient Temp. (°C)
Report Prepared By |  |  | Fazli Wahid Test Inspector
RELAY TESTING INDEX
Sheet | Relay Ref. | Protection Function |  | Relay Type | HV CT | LV CT | ANSI Code | Status
A.1-P | A.1 | 87T Differential Protection – Set 1 (Pre-Test Checks) |  | 7UT6131-1AA0 | 1200/1A | 2400/1A | ANSI 87T | PENDING
A.1-D | A.1 | 87T Differential – Set 1 (Pickup & Stability) |  | 7UT6131-1AA0 | 1200/1A | 2400/1A | ANSI 87T | PENDING
A.1-S | A.1 | 87T Differential – Set 1 (Slope Characteristic) |  | 7UT6131-1AA0 | 1200/1A | 2400/1A | ANSI 87T | PENDING
A.1-H | A.1 | 87T Differential – Set 1 (Harmonic Restraint) |  | 7UT6131-1AA0 | 1200/1A | 2400/1A | ANSI 87T | PENDING
A.1-B | A.1 | Buchholz / OTI / WTI / PRV (Set 1) |  | Mech. Relays | – | – | ANSI 63/26 | PENDING
A.2-P | A.2 | 87T Differential Protection – Set 2 (Pre-Test Checks) |  | 7UT6131-1AB0 | 1200/1A | 1600/1A | ANSI 87T | PENDING
A.2-D | A.2 | 87T Differential – Set 2 (Pickup & Stability) |  | 7UT6131-1AB0 | 1200/1A | 1600/1A | ANSI 87T | PENDING
A.2-S | A.2 | 87T Differential – Set 2 (Slope Characteristic) |  | 7UT6131-1AB0 | 1200/1A | 1600/1A | ANSI 87T | PENDING
A.2-H | A.2 | 87T Differential – Set 2 (Harmonic Restraint) |  | 7UT6131-1AB0 | 1200/1A | 1600/1A | ANSI 87T | PENDING
A.3 | A.3 | HV (220kV) Overcurrent & Earth Fault Protection |  | 7SJ8021 | 1200/1A | – | ANSI 51/51N | PENDING
⚠ SAFETY: All tests performed with transformer de-energised, isolated & earthed. Follow NTDC/WAPDA PTW & safety rules. CT secondaries must be shorted before opening injection circuits.

## A.1-Pre-Test
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.1 Differential Protection Set-1 – Pre-Test Checks & IR Tests
Relay Type: |  | Siemens 7UT6131-5EB92-1AA0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A (HV BCT Core-1) |  |  | LV CT Ratio: |  | 2400/1A (LV BCT Core-1, 7S1-7S3)
HV Rated I: |  | 662.69 A primary |  |  | LV Rated I: |  | 1093.47 A primary
Sheet No: |  | 1 of 10 |  |  | Station:
A. VISUAL & MECHANICAL INSPECTION
No. | Check Item |  |  | Requirement |  | Result | Pass/Fail | Initials
1 | Transformer nameplate verified (250 MVA, 220/132 kV, YNa0d1) |  |  | Per design drawings |  |  | ✓ / ✗
2 | Relay panels physically secured – no damage or loose fittings |  |  | No damage / loose fittings |  |  | ✓ / ✗
3 | Terminal wiring correct per approved scheme drawings (G76001) |  |  | Per approved drawings |  |  | ✓ / ✗
4 | CT/VT polarity markings verified (P1→S1 facing transformer) |  |  | Correct polarity markings |  |  | ✓ / ✗
5 | CT secondary shorting links: removed from circuits under test |  |  | Link status confirmed |  |  | ✓ / ✗
6 | Earth connections: solid and low resistance (< 1 Ω) |  |  | < 1 Ω measured |  |  | ✓ / ✗
7 | DC auxiliary supply voltage within ±10% of rated |  |  | Vdc ± 10% of rated |  |  | ✓ / ✗
8 | Trip circuit fuses / MCBs rated correctly per schedule |  |  | Per protection schedule |  |  | ✓ / ✗
9 | Binary inputs / outputs wired per scheme drawings |  |  | Per drawings |  |  | ✓ / ✗
10 | Relay firmware version noted and approved for use |  |  | Version on record |  |  | ✓ / ✗
11 | All CT/VT secondary burdens within rated limits |  |  | Within CT/VT burden limit |  |  | ✓ / ✗
12 | Relay self-diagnostics healthy (no fault LEDs on power-on) |  |  | All LEDs healthy / green |  |  | ✓ / ✗
13 | Buchholz relay float check & gas collection port clear |  |  | Visually OK |  |  | ✓ / ✗
14 | Oil level / temperature indicators operational and reading normal |  |  | Within normal range |  |  | ✓ / ✗
15 | Pressure Relief Valve (PRV) checked – functional & reset |  |  | Operational |  |  | ✓ / ✗
B. INSULATION RESISTANCE TEST (500 VDC Megger) – IEC 60255-27 Cl. 8.4
No. | Circuit Under Test |  | Test V (VDC) | Min. (MΩ) | Measured Before (MΩ) | Measured After (MΩ) | Temp (°C) | Pass/Fail
1 | 87T Diff – HV CT circuits (1200/1A) to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
2 | 87T Diff – LV CT circuits (2400/1A, 7S1-7S3) to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
3 | REF HV – CT circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
4 | REF LV – CT circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
5 | OC/EF HV Trip circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
6 | OC/EF LV Trip circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
7 | DC Auxiliary supply to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
8 | Binary input circuits to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
9 | VT circuits to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
10 | Relay case / chassis to Earth |  | 500 | ≥ 100 |  |  |  | ✓ / ✗
C. TEST EQUIPMENT RECORD
Equipment |  | Make / Model |  | Serial No. | Cal. Cert. No. | Cal. Due Date | Range Used | Remarks
Secondary Injection Test Set (e.g. Omicron CMC 256/356)
Multimeter / Clamp Meter (True RMS)
Timer / Stop Watch (ms resolution)
Insulation Resistance Tester (500 VDC Megger)
Earth Resistance Tester
CT Test Set (ratio & polarity)
Oscilloscope / Laptop + Relay Software
📋 NOTES, FORMULAS & STANDARDS — PRE-TEST CHECKS ¦ SET-1
📚 APPLICABLE STANDARDS
▪ IEC 60255-27 – General requirements for measuring relays and protection equipment
▪ IEEE C37.90 – Relays and relay systems associated with electric power apparatus
▪ NTDC/WAPDA Protection Panel Inspection & Testing Checklist
📐 KEY FORMULAS
Earth resistance check: R_earth < 1 Ω (use 4-wire Kelvin method or dedicated tester)
DC supply tolerance: V_dc_measured = V_rated ± 10% e.g. 110VDC → acceptable: 99–121 V
IR acceptance: R_insulation ≥ 100 MΩ at 500 VDC (IEC 60255-27 Table 7)
CT burden check: Z_burden(Ω) = V_burden² / S_burden — must be < rated burden of CT
📝 TESTING NOTES & GUIDANCE
• All CT secondary circuits MUST be shorted before disconnecting any wiring.
• Megger test must be done BEFORE any injection tests – a low IR can cause relay maloperation.
• Verify NTDC-approved drawings are the latest revision before starting tests.
• For Set-1: confirm LV CT ratio = 2400/1 at relay address 0207. Set-1 uses Core-1 (7S1-7S3).
• DC auxiliary voltage measurement must be made at RELAY terminals, not at DC panel.
• Ambient temperature must be recorded – IR readings are temperature dependent.
• All test equipment calibration certificates must be valid and on file before testing starts.
• If any IR reading < 100 MΩ – STOP, find and rectify the fault before proceeding.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.1-Diff Pickup
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.1 87T Differential Protection Set-1 – Pickup, Drop-off & Stability
Relay Type: |  | Siemens 7UT6131-5EB92-1AA0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV BCT Core-1 |  |  | LV CT Ratio: |  | 2400/1A LV BCT Core-1 (7S1-7S3)
HV Rated I: |  | I_NOb HV=0.552A |  |  | LV Rated I: |  | I_NOb LV=0.456A
Sheet No: |  | 2 of 10 |  |  | Station:
A. RELAY SETTINGS & TRANSFORMER DATA
Transformer Rating |  |  | 250 MVA, 220/132 kV, YNa0d1, %Z=15.57%
HV Effective Voltage |  |  | U_N = 2×(242×198.01)/(242+198.01) = 217.8 kV (OLTC harmonic mean)
HV Full Load Current |  |  | I_FL_HV = 250,000/(√3×217.8) = 662.69 A primary
LV Full Load Current |  |  | I_FL_LV = 250,000/(√3×132) = 1093.47 A primary
HV CT Ratio (Set-1) |  |  | 1200/1A – BCT Core-1 ¦ Secondary base I_NOb = 662.69/1200 = 0.552 A
LV CT Ratio (Set-1) |  |  | 2400/1A – BCT Core-1 (7S1-7S3) ¦ Secondary base I_NOb = 1093.47/2400 = 0.456 A
I-Diff > Pickup |  |  | 25% of I_NOb ¦ HV side: 0.25×0.552 = 0.138 A ¦ LV side: 0.25×0.456 = 0.114 A
Apply Current (102%) |  |  | HV: 0.138×1.02 = 0.141 A ¦ LV: 0.114×1.02 = 0.116 A
Drop-off Current (95%) |  |  | HV: 0.138×0.95 = 0.131 A ¦ LV: 0.114×0.95 = 0.108 A
Operate Time (I-Diff) |  |  | < 30 ms at 2× threshold (instantaneous, no intentional delay – addr 1226A = 0)
Relay Address 0207 |  |  | LV CT = 2400 (SET-1 CRITICAL – must NOT be 1600)
Vector Group (Relay) |  |  | YNa0d1 – relay compensates internally; no external interposing CTs needed
B. HV SIDE PICKUP & DROP-OFF TEST (I-Diff Set = 0.138 A = 25% × 0.552 A)
Phase | Calc. Pickup (A) | Applied (102%) (A) | Pickup Observed (A) | Contact Time (ms) | Drop-off Observed (A) | Drop-off Time (ms) | Error (%) | Pass/Fail
L1 – Red | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓ / ✗
L2 – Yellow | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓ / ✗
L3 – Blue | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓ / ✗
C. LV SIDE PICKUP & DROP-OFF TEST (I-Diff Set = 0.114 A = 25% × 0.456 A)
Phase | Calc. Pickup (A) | Applied (102%) (A) | Pickup Observed (A) | Contact Time (ms) | Drop-off Observed (A) | Drop-off Time (ms) | Error (%) | Pass/Fail
L1 – Red | 0.114 | 0.116 |  |  | 0.108 |  |  | ✓ / ✗
L2 – Yellow | 0.114 | 0.116 |  |  | 0.108 |  |  | ✓ / ✗
L3 – Blue | 0.114 | 0.116 |  |  | 0.108 |  |  | ✓ / ✗
D. STABILITY TEST (Through-Fault – Balanced – Relay Must NOT Trip)
Test Condition |  | HV I-R (A) | HV I-Y (A) | HV I-B (A) | LV I-R (A) | LV I-Y (A) | LV I-B (A) | Pass/Fail
HV Energise only (LV = 0 A) |  | 0.552 | 0.552 | 0.552 | 0 | 0 | 0 | ✓ / ✗
LV Energise only (HV = 0 A) |  | 0 | 0 | 0 | 0.456 | 0.456 | 0.456 | ✓ / ✗
Full Load Both Sides (100%) |  | 0.552 | 0.552 | 0.552 | 0.456 | 0.456 | 0.456 | ✓ / ✗
150% Load Both Sides |  | 0.828 | 0.828 | 0.828 | 0.684 | 0.684 | 0.684 | ✓ / ✗
E. OPERATE TIME TEST (Inject 2× I-Diff = 0.276 A on HV Side, LV Open)
Phase | Injected I (A) | Expected Time | Time-1 (ms) | Time-2 (ms) | Time-3 (ms) | Average (ms) | LED / Indication | Pass/Fail
L1 – Red | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓ / ✗
L2 – Yellow | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓ / ✗
L3 – Blue | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓ / ✗
📋 NOTES, FORMULAS & STANDARDS — 87T PICKUP & STABILITY ¦ SET-1
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Functional requirements for transformer differential protection
▪ IEC 60076-1 – Power Transformers: General
▪ ANSI/IEEE C37.90 – Relays associated with electric power apparatus
▪ NTDC Protection Relay Testing & Commissioning Guidelines
📐 KEY FORMULAS
U_N (effective HV) = 2×(U_max×U_min)/(U_max+U_min) = 2×(242×198.01)/(242+198.01) = 217.8 kV
I_FL_HV = S/(√3×U_N) = 250,000/(1.732×217.8) = 662.69 A (primary)
I_FL_LV = S/(√3×U_LV) = 250,000/(1.732×132) = 1093.47 A (primary)
I_NOb_HV = I_FL_HV/CT_HV = 662.69/1200 = 0.552 A (secondary base)
I_NOb_LV = I_FL_LV/CT_LV = 1093.47/2400 = 0.456 A (secondary base, Set-1)
I-Diff pickup = 25% × I_NOb → HV: 0.25×0.552 = 0.138 A ¦ LV: 0.25×0.456 = 0.114 A
Apply current = 102% × pickup → HV: 1.02×0.138 = 0.141 A ¦ LV: 1.02×0.114 = 0.116 A
Drop-off = 95% × pickup → HV: 0.95×0.138 = 0.131 A ¦ LV: 0.95×0.114 = 0.108 A
Operate time test level = 2× pickup → HV: 2×0.138 = 0.276 A ¦ Expected: < 30 ms
I_diff (through-fault, balanced) = ¦I_HV - I_LV¦ ≈ 0 A → relay stable
I_diff (internal fault) = ¦I_HV - I_LV¦ >> 0 → relay trips
📝 TESTING NOTES & GUIDANCE
• Set-1 uses LV CT = 2400/1 (Core-1, 7S1-7S3). Relay address 0207 MUST = 2400.
• CT polarity: star point must face the protected object (transformer) on BOTH sides.
• Pickup tolerance: ±5% of set value per IEC 60255-151 (0.131–0.145 A for HV).
• Operate time: < 30 ms (instantaneous, address 1226A = 0, no intentional delay).
• Stability test: inject HV at 0°, LV at 180° (opposition). Relay MUST NOT trip.
• If relay trips during stability test → CT polarity is wrong. Check wiring.
• Max tap changer error = 10% → I_diff error ≈ 10.02% → 25% setting gives 2.5× margin.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.1-Slope Test
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.1 87T Differential Set-1 – Slope Characteristic Test
Relay Type: |  | Siemens 7UT6131-5EB92-1AA0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV |  |  | LV CT Ratio: |  | 2400/1A LV
HV Rated I: |  | Slope-1=30% ¦ Base-1=0.0 |  |  | LV Rated I: |  | Slope-2=60% ¦ Base-2=2.5×In
Sheet No: |  | 3 of 10 |  |  | Station:
PROCEDURE: Inject I_HV at 0° and I_LV at 180° (opposition) simultaneously. Relay stable when balanced. Slowly increase I_HV while holding I_LV to create I_diff. Record I_diff and I_bias at trip point. % Slope = (ΔI_diff / ΔI_bias) × 100
A. SLOPE-1 TEST (I-bias < 2.5 × In) – Expected Slope ≈ 30%
Test Point | I-Bias (×In) | HV I (A) at 0° | LV I (A) at 180° | I-Diff at Trip (A) | I-Bias at Trip (A) | % Slope Calc. | Phase | Pass/Fail
0.5 × In (Slope 1 lower) | 0.5 | 0.317 | 0.235 |  |  | ≈ 30% | R/Y/B | ✓/✗
1.0 × In (Slope 1 mid) | 1 | 0.635 | 0.469 |  |  | ≈ 30% | R/Y/B | ✓/✗
2.0 × In (Slope 1 upper) | 2 | 1.27 | 0.938 |  |  | ≈ 30% | R/Y/B | ✓/✗
B. SLOPE-2 TEST (I-bias > 2.5 × In – CT Saturation Region) – Expected Slope ≈ 60%
Test Point | I-Bias (×In) | HV I (A) at 0° | LV I (A) at 180° | I-Diff at Trip (A) | I-Bias at Trip (A) | % Slope Calc. | Phase | Pass/Fail
2.5 × In (Slope 2 start) | 2.5 | 1.587 | 1.173 |  |  |  | R/Y/B | ✓/✗
3.0 × In (Slope 2 mid) | 3 | 1.946 | 1.366 |  |  |  | R/Y/B | ✓/✗
4.0 × In (Slope 2 upper) | 4 | 2.663 | 1.753 |  |  |  | R/Y/B | ✓/✗
C. SLOPE SUMMARY
Parameter |  | Expected | Phase R | Phase Y | Phase B | Average | Tolerance | Pass/Fail
% Slope 1 (I_bias < 2.5×In) |  | ≈ 30% |  |  |  |  | ±5% | ✓/✗
% Slope 2 (I_bias > 2.5×In) |  | ≈ 60% |  |  |  |  | ±5% | ✓/✗
Base Point 1 |  | 0.0 × In |  |  |  |  | Fixed | ✓/✗
Base Point 2 (changeover) |  | 2.5 × In |  |  |  |  | Fixed | ✓/✗
I-Diff >> (Unrestrained high-set) |  | 10.0 × In |  |  |  |  | Not blocked by harmonics | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — 87T SLOPE CHARACTERISTIC ¦ SET-1
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Slope characteristic requirements for 87T protection
▪ IEC 60909 – Short-circuit currents in three-phase AC systems
📐 KEY FORMULAS
I_bias (restraining current) = (¦I_HV_sec¦ + ¦I_LV_sec¦) / 2
I_diff (differential current) = ¦I_HV_sec − I_LV_sec¦
Slope-1 trip boundary (I_bias < 2.5×In): I_diff_trip = 0.30 × I_bias + 0.0 (Base Pt 1 = 0)
Slope-2 trip boundary (I_bias > 2.5×In): I_diff_trip = 0.60 × I_bias − offset
Measured slope = (I_diff_B − I_diff_A) / (I_bias_B − I_bias_A) × 100 [use 2 trip points, same slope]
HV injection = I_bias + I_diff/2 ¦ LV injection = I_bias − I_diff/2 (HV: 0°, LV: 180°)
At slope boundary: I_diff = Slope × I_bias → calculate HV & LV injection currents accordingly
📝 TESTING NOTES & GUIDANCE
• Slope-1 = 30%: provides security against tap changer error (10%) + CT errors (total ≈10.02%).
• Slope-2 = 60%: provides security against CT saturation during heavy external through-fault currents.
• Changeover from Slope-1 to Slope-2 at I_bias = 2.5 × In (CT saturation risk threshold).
• I-Diff >> = 10.0 × In: unrestrained element, NOT blocked by harmonics. Clears severe faults instantly.
• Tolerance: measured slope within ±5% of set value (30%→25–35%, 60%→55–65%).
• If measured slope differs significantly from expected: verify CT ratios, polarity and relay addressing.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.1-Harmonic
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.1 87T Differential Set-1 – Harmonic Restraint Test
Relay Type: |  | 7UT6131-5EB92-1AA0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV |  |  | LV CT Ratio: |  | 2400/1A LV
HV Rated I: |  | 2nd Harm=15% ¦ 5th Harm=40% |  |  | LV Rated I: |  | Cross-block=25 cycles
Sheet No: |  | 4 of 10 |  |  | Station:
2ND HARMONIC (100 Hz): If I_2nd/I_fund > 15% → BLOCK (inrush restraint – NO TRIP) ¦ 5TH HARMONIC (250 Hz): If I_5th/I_fund > 40% → BLOCK (overexcitation restraint – NO TRIP) ¦ Test set must inject two frequencies simultaneously on the same channel.
A. 2nd HARMONIC RESTRAINT TEST (Inrush – 100 Hz) ¦ Block Threshold = 15%
Phase | Fund. I (A) 50 Hz | Fund. Angle | Harm. I (A) 100 Hz | Harm. Angle | Ratio (Harm/Fund %) | Expected Response | Actual Response | Pass/Fail
HV L1-Red | 0.207 | 0° | 0.0331 | 0° | 16% | NO TRIP |  | ✓/✗
HV L2-Yellow | 0.207 | -120° | 0.0331 | -120° | 16% | NO TRIP |  | ✓/✗
HV L3-Blue | 0.207 | 120° | 0.0331 | 120° | 16% | NO TRIP |  | ✓/✗
LV L1-Red | 0.171 | 180° | 0.0274 | 180° | 16% | NO TRIP |  | ✓/✗
LV L2-Yellow | 0.171 | 60° | 0.0274 | 60° | 16% | NO TRIP |  | ✓/✗
LV L3-Blue | 0.171 | 300° | 0.0274 | 300° | 16% | NO TRIP |  | ✓/✗
B. 5th HARMONIC RESTRAINT TEST (Overexcitation – 250 Hz) ¦ Block Threshold = 40%
Phase | Fund. I (A) 50 Hz | Fund. Angle | Harm. I (A) 250 Hz | Harm. Angle | Ratio (Harm/Fund %) | Expected Response | Actual Response | Pass/Fail
HV L1-Red | 0.0552 | 0° | 0.0231 | 0° | 42% | NO TRIP |  | ✓/✗
HV L2-Yellow | 0.0552 | -120° | 0.0231 | -120° | 42% | NO TRIP |  | ✓/✗
HV L3-Blue | 0.0552 | 120° | 0.0231 | 120° | 42% | NO TRIP |  | ✓/✗
LV L1-Red | 0.0456 | 180° | 0.0192 | 180° | 42% | NO TRIP |  | ✓/✗
LV L2-Yellow | 0.0456 | 60° | 0.0192 | 60° | 42% | NO TRIP |  | ✓/✗
LV L3-Blue | 0.0456 | 300° | 0.0192 | 300° | 42% | NO TRIP |  | ✓/✗
C. HARMONIC BLOCKING THRESHOLD VERIFICATION (above & below threshold)
Harmonic | Threshold | Level ABOVE threshold | Expected | Result | Level BELOW threshold | Expected | Result | Pass/Fail
2nd Harm (Inrush) | 15% of Fund | 0.0331 A (16%) | NO TRIP |  | 0.0248 A (12%) | TRIP |  | ✓/✗
5th Harm (Overexcit.) | 40% of Fund | 0.0231 A (42%) | NO TRIP |  | 0.0193 A (35%) | TRIP |  | ✓/✗
D. CROSS-BLOCK FUNCTION TEST (2nd Harmonic in one phase blocks all 3 phases)
PROCEDURE: Inject fundamental + 2nd harmonic > 15% into HV Phase R (R is restrained). Simultaneously inject I_diff ABOVE threshold into HV Phase Y (no harmonic on Y). Phase Y MUST also be blocked for 25 cycles (500 ms). After 500 ms, if I_diff on Y still above threshold → relay trips Y.
Step | Description |  |  | Expected |  | Observed | Time (ms) | Pass/Fail
Step 1 | Phase R: inject 0.207A @50Hz + 0.033A @100Hz (16% > 15%) |  |  | Phase R: BLOCK active |  |  |  | ✓/✗
Step 2 | Phase Y: inject 0.276A @50Hz (2× I-Diff), no harmonic |  |  | Phase Y: also BLOCKED (cross-block) |  |  |  | ✓/✗
Step 3 | After 25 cycles (500ms): Phase Y I_diff still > threshold |  |  | Phase Y: TRIPS after 500ms |  |  |  | ✓/✗
Step 4 | Phase R harmonic removed after cross-block expires |  |  | All phases: unblock & operate normally |  |  |  | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — 87T HARMONIC RESTRAINT ¦ SET-1
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Harmonic restraint requirements for transformer differential protection
▪ IEEE C37.91 – Guide for protecting power transformers
📐 KEY FORMULAS
2nd Harmonic ratio = I_2nd(A) / I_fund(A) × 100 → if > 15%: BLOCK (inrush detected)
5th Harmonic ratio = I_5th(A) / I_fund(A) × 100 → if > 40%: BLOCK (overexcitation detected)
Cross-block duration = 25 AC cycles × (1/50 Hz) = 25 × 20 ms = 500 ms
Test level above (NO TRIP): 2nd harm = 16% of fund → HV: 0.207×0.16 = 0.033 A at 100 Hz
Test level below (TRIP): 2nd harm = 12% of fund → HV: 0.207×0.12 = 0.025 A at 100 Hz
5th harm above (NO TRIP): 42% → HV: 0.055×0.42 = 0.023 A at 250 Hz
5th harm below (TRIP): 35% → HV: 0.055×0.35 = 0.019 A at 250 Hz
📝 TESTING NOTES & GUIDANCE
• Test set must support simultaneous dual-frequency injection (e.g. Omicron CMC 256/356 or Doble F6150).
• 2nd harmonic (100 Hz) is caused by transformer inrush magnetising current on energisation.
• 5th harmonic (250 Hz) is caused by overexcitation (high V/f ratio). 3rd is eliminated by delta winding.
• I-Diff >> = 10.0×In is NOT blocked by harmonics – severe faults must trip even during inrush.
• Add-on stabilisation (addr 1261A) = 4.5×In prevents false trip from CT saturation in first half-cycle.
• Cross-block (addr 1272 = 25 cycles) handles simultaneous inrush + genuine fault in different phases.
• Both above-threshold (NO TRIP) and below-threshold (TRIP) tests must be performed for both harmonics.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.1-Buchholz
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.1 Buchholz Relay, OTI, WTI, PRV & Oil Level Tests (ANSI 26/63)
Relay Type: |  | Mechanical Relays / Sensors |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | N/A |  |  | LV CT Ratio: |  | N/A
HV Rated I: |  | IEC 60076-2 / 3 |  |  | LV Rated I: |  | ANSI 26 / 63
Sheet No: |  | 5 of 10 |  |  | Station:
A. BUCHHOLZ RELAY TEST (Main Tank & OLTC)
No. | Test Description |  |  | Requirement |  | Contact Verified | Alarm/Trip Operated | Pass/Fail
1 | Main Tank Buchholz – Float test – ALARM (gas accumulation simulation via test cock) |  |  | Alarm contact closes |  |  |  | ✓/✗
2 | Main Tank Buchholz – Float test – TRIP (surge/heavy fault via test rod actuation) |  |  | Trip contact closes |  |  |  | ✓/✗
3 | OLTC Buchholz – Alarm float test (diverter switch compartment) |  |  | Alarm operated |  |  |  | ✓/✗
4 | OLTC Buchholz – Trip float test |  |  | Trip operated |  |  |  | ✓/✗
5 | Buchholz relay reset / self-check after test |  |  | Relay resets cleanly |  |  |  | ✓/✗
6 | Alarm circuit continuity check to control room / SCADA |  |  | SCADA alarm received |  |  |  | ✓/✗
7 | Trip circuit continuity check – to CB trip coil |  |  | CB trips confirmed |  |  |  | ✓/✗
B. OIL TEMPERATURE INDICATOR (OTI) & WINDING TEMPERATURE INDICATOR (WTI)
Device | Alarm Set (°C) | Trip Set (°C) | Alarm Operated (°C) | Trip Operated (°C) | Reset (°C) | Contact Checked | SCADA Confirmed | Pass/Fail
OTI – Main Tank Oil | 85°C | 95°C | [5 empty] | ✓/✗
WTI – HV Winding | 100°C | 110°C | [5 empty] | ✓/✗
WTI – LV Winding | 100°C | 110°C | [5 empty] | ✓/✗
OLTC Oil Temperature | 85°C | 95°C | [5 empty] | ✓/✗
C. PRESSURE RELIEF VALVE (PRV) & OIL LEVEL INDICATOR
No. | Device / Test |  |  | Requirement |  | Contact Verified | Result | Pass/Fail
1 | PRV Trip Contact – Manually actuate test rod (WITHOUT releasing oil) |  |  | Contact closes → CB trips |  |  |  | ✓/✗
2 | Oil Level Low – ALARM: manually depress/lift float to LOW position |  |  | ALARM contact closes |  |  |  | ✓/✗
3 | Oil Level Very Low – TRIP: further depress float to VERY LOW |  |  | TRIP contact closes → CB trips |  |  |  | ✓/✗
4 | PRV Reset after test rod released |  |  | Contact resets cleanly |  |  |  | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — BUCHHOLZ & MECHANICAL PROTECTION ¦ SET-1
📚 APPLICABLE STANDARDS
▪ IEC 60076-2 – Temperature rise for liquid-immersed transformers
▪ IEC 60076-3 – Insulation levels, dielectric tests for transformers
▪ NTDC Substation Equipment Maintenance & Testing Guidelines
📐 KEY FORMULAS
Buchholz test method: Open test cock → oil drops → upper float tilts → ALARM contact
Buchholz surge test: Press test rod → lower paddle deflects → TRIP contact
OTI/WTI test: Rotate temperature pointer to alarm/trip set-point → micro-switch activates
PRV test: Press test rod on valve body → micro-switch closes → TRIP contact
Oil level: Float at LOW → ALARM ¦ Float at VERY LOW → TRIP
📝 TESTING NOTES & GUIDANCE
• Never open Buchholz test cock while transformer is energised – risk of explosive oil-air mixture.
• Never operate PRV disc by hand on energised transformer – pressurised hot oil will spray out.
• OTI/WTI mechanical pointer test is preferred – faster and does not require heating up.
• All TRIP contacts must energise the CB trip coil and CB must actually open (verify position indicator).
• All devices must RESET cleanly after removing test stimulus – no latched or sticky contacts.
• SCADA/DCS must confirm correct alarm label and transformer tag number for each device.
• Record ambient temperature during OTI/WTI test – readings are temperature dependent.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.2-Pre-Test
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.2 Differential Protection Set-2 – Pre-Test Checks & IR Tests
Relay Type: |  | Siemens 7UT6131-5EB92-1AB0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A (HV Lower/Mid CT Core-3) |  |  | LV CT Ratio: |  | 1600/1A (LV BCT Core-3, 3S1-3S4) ← SET-2
HV Rated I: |  | I_NOb HV=0.552A |  |  | LV Rated I: |  | I_NOb LV=0.683A
Sheet No: |  | 6 of 10 |  |  | Station:
⚠ SET-2 KEY DIFFERENCE: LV CT = 1600/1 (Core-3, 3S1-3S4) vs Set-1 LV CT = 2400/1. I_NOb_LV (Set-2) = 0.683 A vs 0.456 A (Set-1). Relay address 0207 MUST = 1600. Wrong CT ratio → false differential → maloperation.
A. VISUAL & MECHANICAL INSPECTION (Set-2 Specific)
1 | Transformer nameplate verified (250 MVA, 220/132 kV, YNa0d1) |  |  |  | Per design drawings |  |  | ✓/✗
2 | Relay panels physically secured – no damage or loose fittings |  |  |  | No damage / loose fittings |  |  | ✓/✗
3 | Terminal wiring correct per approved scheme drawings |  |  |  | Per approved drawings |  |  | ✓/✗
4 | CT/VT polarity markings verified (P1→S1 facing transformer) |  |  |  | Correct polarity markings |  |  | ✓/✗
5 | LV CT Ratio confirmed as 1600/1 (Core-3, terminals 3S1-3S4) |  |  |  | CT ratio: 1600/1 confirmed |  |  | ✓/✗
6 | HV CT Ratio confirmed as 1200/1 (Lower CT Core-3 / Mid CT Core-3) |  |  |  | CT ratio: 1200/1 confirmed |  |  | ✓/✗
7 | Relay address 0207 = 1600 (NOT 2400) |  |  |  | Address 0207 = 1600 verified |  |  | ✓/✗
8 | CT secondary shorting links: removed from circuits under test |  |  |  | Link status confirmed |  |  | ✓/✗
9 | Earth connections solid and low resistance (< 1 Ω) |  |  |  | < 1 Ω measured |  |  | ✓/✗
10 | DC auxiliary supply voltage within ±10% of rated |  |  |  | Vdc ± 10% of rated |  |  | ✓/✗
11 | Relay self-diagnostics healthy (no fault LEDs) |  |  |  | All LEDs healthy / green |  |  | ✓/✗
12 | Relay firmware version noted and approved |  |  |  | Version on record |  |  | ✓/✗
B. INSULATION RESISTANCE TEST (500 VDC Megger) – IEC 60255-27 Cl. 8.4
No. | Circuit Under Test |  | Test V (VDC) | Min. (MΩ) | Meas. Before (MΩ) | Meas. After (MΩ) | Temp (°C) | Pass/Fail
1 | 87T Diff – HV CT circuits (1200/1A, Core-3) to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
2 | 87T Diff – LV CT circuits (1600/1A, Core-3, 3S1-3S4) to Earth ← SET-2 |  | 500 | ≥ 100 |  |  |  | ✓/✗
3 | REF HV – CT circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
4 | REF LV – CT circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
5 | OC/EF HV Trip circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
6 | OC/EF LV Trip circuit to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
7 | DC Auxiliary supply to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
8 | Binary input circuits to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
9 | VT circuits to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
10 | Relay case / chassis to Earth |  | 500 | ≥ 100 |  |  |  | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — PRE-TEST CHECKS ¦ SET-2
📚 APPLICABLE STANDARDS
▪ IEC 60255-27 – General requirements, insulation tests for protection relays
▪ IEEE C37.90 – Relay and relay systems protection
📐 KEY FORMULAS
I_NOb_LV (Set-2) = I_FL_LV / CT_LV = 1093.47 / 1600 = 0.683 A (secondary base, 1600/1A)
I_NOb_LV (Set-1) = 1093.47 / 2400 = 0.456 A (secondary base, 2400/1A) — DIFFERENT
LV I-Diff pickup (Set-2) = 25% × 0.683 = 0.171 A vs Set-1 = 0.114 A
IR test: R_insulation ≥ 100 MΩ at 500 VDC
📝 TESTING NOTES & GUIDANCE
• CRITICAL: Set-2 LV CT = 1600/1 (terminals 3S1-3S4). Address 0207 MUST = 1600.
• Set-1 uses 2400/1 (7S1-7S3). Set-2 uses 1600/1 (3S1-3S4). Completely different cores.
• Wrong LV CT ratio causes false differential on load current → nuisance trip.
• CT polarity star point must face transformer on both HV and LV sides.
• If relay address 0207 is found set to 2400 instead of 1600 → correct before testing.
• All CT secondary circuits must be shorted before disconnecting any wiring.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.2-Diff Pickup
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.2 87T Differential Protection Set-2 – Pickup, Drop-off & Stability
Relay Type: |  | Siemens 7UT6131-5EB92-1AB0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV (Core-3) |  |  | LV CT Ratio: |  | 1600/1A LV (Core-3, 3S1-3S4)
HV Rated I: |  | I_NOb HV=0.552A |  |  | LV Rated I: |  | I_NOb LV=0.683A
Sheet No: |  | 7 of 10 |  |  | Station:
⚠ SET-2 vs SET-1 KEY DIFFERENCE: LV CT = 1600/1 (not 2400/1). LV I_NOb = 0.683 A (not 0.456 A). LV I-Diff pickup = 0.171 A (not 0.114 A). Stability test LV current at 150% = 1.025 A (not 0.684 A).
A. RELAY SETTINGS & CT DATA (Set-2 Specific)
HV CT Ratio (Set-2) |  |  | 1200/1A – Lower CT Core-3 / Mid CT Core-3 ¦ I_NOb_HV = 662.69/1200 = 0.552 A
LV CT Ratio (Set-2) |  |  | 1600/1A – BCT Core-3 (3S1-3S4) ¦ I_NOb_LV = 1093.47/1600 = 0.683 A ← SET-2
I-Diff > Pickup (HV) |  |  | 25% × 0.552 = 0.138 A ¦ Apply: 0.141 A (102%) ¦ Drop-off: 0.131 A (95%)
I-Diff > Pickup (LV) |  |  | 25% × 0.683 = 0.171 A ¦ Apply: 0.174 A (102%) ¦ Drop-off: 0.162 A (95%)
Operate Time |  |  | < 30 ms at 2× threshold (address 1226A = 0, instantaneous)
Stability Test (100%) |  |  | HV: 0.552 A ¦ LV: 0.683 A (both sides simultaneously, HV at 0°, LV at 180°)
Stability Test (150%) |  |  | HV: 0.828 A ¦ LV: 1.025 A (150% of rated – relay must NOT trip)
Address 0207
B. HV SIDE PICKUP & DROP-OFF TEST (I-Diff Set = 0.138 A – same as Set-1)
Phase | Calc. Pickup (A) | Applied (102%) (A) | Pickup Observed (A) | Contact Time (ms) | Drop-off Observed (A) | Drop-off Time (ms) | Error (%) | Pass/Fail
L1 – Red | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓/✗
L2 – Yellow | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓/✗
L3 – Blue | 0.138 | 0.141 |  |  | 0.131 |  |  | ✓/✗
C. LV SIDE PICKUP & DROP-OFF TEST (I-Diff Set = 0.171 A ← SET-2 DIFFERENT from Set-1)
Phase | Calc. Pickup (A) | Applied (102%) (A) | Pickup Observed (A) | Contact Time (ms) | Drop-off Observed (A) | Drop-off Time (ms) | Error (%) | Pass/Fail
L1 – Red | 0.171 | 0.174 |  |  | 0.162 |  |  | ✓/✗
L2 – Yellow | 0.171 | 0.174 |  |  | 0.162 |  |  | ✓/✗
L3 – Blue | 0.171 | 0.174 |  |  | 0.162 |  |  | ✓/✗
D. STABILITY TEST (Through-Fault – Relay Must NOT Trip)
Test Condition |  | HV I-R (A) | HV I-Y (A) | HV I-B (A) | LV I-R (A) | LV I-Y (A) | LV I-B (A) | Pass/Fail
HV Energise only (LV = 0 A) |  | 0.552 | 0.552 | 0.552 | 0 | 0 | 0 | STABLE ✓
LV Energise only (HV = 0 A) |  | 0 | 0 | 0 | 0.683 | 0.683 | 0.683 | STABLE ✓
Full Load Both Sides (100%) |  | 0.552 | 0.552 | 0.552 | 0.683 | 0.683 | 0.683 | STABLE ✓
150% Load Both Sides |  | 0.828 | 0.828 | 0.828 | 1.025 | 1.025 | 1.025 | STABLE ✓
E. OPERATE TIME TEST (Inject 2× I-Diff = 0.276 A on HV Side, LV Open)
Phase | Injected I (A) | Expected | Time-1 (ms) | Time-2 (ms) | Time-3 (ms) | Average (ms) | LED Confirmed | Pass/Fail
L1–Red | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓/✗
L2–Yellow | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓/✗
L3–Blue | 0.276 | < 30 ms |  |  |  |  | TRIP LED ✓ | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — 87T PICKUP & STABILITY ¦ SET-2
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Transformer differential protection functional requirements
▪ IEC 60076-1 – Power Transformers: General requirements
📐 KEY FORMULAS
I_NOb_LV (Set-2) = I_FL_LV / CT_LV = 1093.47 / 1600 = 0.683 A (Set-1: 0.456 A, different)
LV I-Diff pickup (Set-2) = 25% × 0.683 = 0.171 A (Set-1: 0.114 A)
LV drop-off (Set-2) = 95% × 0.171 = 0.162 A (Set-1: 0.108 A)
Apply LV test current = 102% × 0.171 = 0.174 A
Stability test LV at 150% = 1.5 × 0.683 = 1.025 A (Set-1: 0.684 A)
HV pickup same as Set-1: I_NOb_HV = 0.552 A, I-Diff_HV = 0.138 A
📝 TESTING NOTES & GUIDANCE
• Set-2 LV CT = 1600/1 (Core-3, 3S1-3S4). This is the ONLY key difference from Set-1.
• All HV side values are identical to Set-1 (HV CT = 1200/1 in both).
• VERIFY relay address 0207 = 1600 before starting any injection tests.
• Stability test LV injection at full load = 0.683 A (not 0.456 A as in Set-1).
• If stability test fails (relay trips) – check CT polarity wiring, not CT ratio (same check as Set-1).
• Pickup tolerance: ±5% → LV: 0.162–0.180 A acceptable range.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.2-Slope Test
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.2 87T Differential Set-2 – Slope Characteristic Test
Relay Type: |  | Siemens 7UT6131-5EB92-1AB0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV |  |  | LV CT Ratio: |  | 1600/1A LV
HV Rated I: |  | Slope-1=30% ¦ Base-1=0.0 |  |  | LV Rated I: |  | Slope-2=60% ¦ Base-2=2.5×In
Sheet No: |  | 8 of 10 |  |  | Station:
PROCEDURE: HV at 0°, LV at 180° (opposing). Start balanced (I_HV ≈ I_LV in normalised). Slowly increase I_HV while keeping I_LV constant. Record I_diff and I_bias at trip point. NOTE: Set-2 uses I_N2=0.683A for LV normalisation (vs 0.456A for Set-1).
A. SLOPE-1 TEST (I-bias < 2.5 × In) – Expected Slope ≈ 30%
Test Point | I-Bias (×In) | HV I (A) at 0° | LV I (A) at 180° | I-Diff at Trip (A) | I-Bias at Trip (A) | % Slope Calc. | Phase | Pass/Fail
0.5 × In (Slope 1 lower) | 0.5 | 0.318 | 0.235 |  |  |  | R/Y/B | ✓/✗
1.0 × In (Slope 1 mid) | 1 | 0.635 | 0.469 |  |  |  | R/Y/B | ✓/✗
2.0 × In (Slope 1 upper) | 2 | 1.27 | 0.939 |  |  |  | R/Y/B | ✓/✗
B. SLOPE-2 TEST (I-bias > 2.5 × In) – Expected Slope ≈ 60%
Test Point | I-Bias (×In) | HV I (A) at 0° | LV I (A) at 180° | I-Diff at Trip (A) | I-Bias at Trip (A) | % Slope Calc. | Phase | Pass/Fail
2.5 × In (Slope 2 start) | 2.5 | 1.795 | 0.966 |  |  |  | R/Y/B | ✓/✗
3.0 × In (Slope 2 mid) | 3 | 2.154 | 1.16 |  |  |  | R/Y/B | ✓/✗
4.0 × In (Slope 2 upper) | 4 | 2.872 | 1.546 |  |  |  | R/Y/B | ✓/✗
C. SLOPE SUMMARY
Parameter |  | Expected | Phase R | Phase Y | Phase B | Average | Tolerance | Pass/Fail
% Slope 1 (I_bias < 2.5×In) |  | ≈ 30% |  |  |  |  | ±5% | ✓/✗
% Slope 2 (I_bias > 2.5×In) |  | ≈ 60% |  |  |  |  | ±5% | ✓/✗
Base Point 1 |  | 0.0 × In |  |  |  |  | Fixed | ✓/✗
Base Point 2 (changeover) |  | 2.5 × In |  |  |  |  | Fixed | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — 87T SLOPE CHARACTERISTIC ¦ SET-2
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Slope characteristic requirements for 87T protection
▪ IEC 60909 – Short-circuit currents in three-phase AC systems
📐 KEY FORMULAS
I_NOb_HV = 0.552 A (HV CT = 1200/1, same as Set-1)
I_NOb_LV (Set-2) = 1093.47/1600 = 0.683 A (LV CT = 1600/1, DIFFERENT from Set-1)
I_bias = (¦I_HV_sec¦ + ¦I_LV_sec¦) / 2 (in normalised units for relay display)
I_diff = ¦I_HV_sec − I_LV_sec¦
Slope-1: I_diff_trip = 0.30 × I_bias (valid for I_bias < 2.5×In)
Slope-2: I_diff_trip = 0.60 × I_bias − offset (valid for I_bias > 2.5×In)
% Slope = (I_diff_B − I_diff_A)/(I_bias_B − I_bias_A) × 100
📝 TESTING NOTES & GUIDANCE
• For Set-2: LV normalised base = 0.683 A. Test currents differ from Set-1 on LV side.
• HV injection currents same as Set-1 (HV CT ratio unchanged).
• Slope selection: Slope-1=30% provides margin above total error ≈21% (Set-2, larger LV CT error).
• Slope-2=60% prevents false trips during CT saturation on external heavy faults.
• Tolerance: ±5% on measured slope percentage at all three test points per slope.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.2-Harmonic
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.2 87T Differential Set-2 – Harmonic Restraint Test
Relay Type: |  | 7UT6131-5EB92-1AB0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A HV |  |  | LV CT Ratio: |  | 1600/1A LV
HV Rated I: |  | 2nd Harm=15% ¦ 5th Harm=40% |  |  | LV Rated I: |  | Cross-block=25 cyc ¦ Add-on Stab=4.5×In
Sheet No: |  | 9 of 10 |  |  | Station:
2ND HARMONIC (100 Hz): I_2nd/I_fund > 15% → BLOCK. 5TH HARMONIC (250 Hz): I_5th/I_fund > 40% → BLOCK. Set-2 LV currents differ from Set-1 due to LV CT = 1600/1A (I_NOb = 0.683 A).
A. 2nd HARMONIC RESTRAINT TEST (Inrush – 100 Hz) ¦ Threshold = 15%
Phase | Fund. I (A) 50 Hz | Fund. Angle | Harm. I (A) 100 Hz | Harm. Angle | Ratio (%) | Expected | Actual | Pass/Fail
HV L1-Red | 0.207 | 0° | 0.0331 | 0° | 16% | NO TRIP |  | ✓/✗
HV L2-Yellow | 0.207 | -120° | 0.0331 | -120° | 16% | NO TRIP |  | ✓/✗
HV L3-Blue | 0.207 | 120° | 0.0331 | 120° | 16% | NO TRIP |  | ✓/✗
LV L1-Red | 0.256 | 180° | 0.041 | 180° | 16% | NO TRIP |  | ✓/✗
LV L2-Yellow | 0.256 | 60° | 0.041 | 60° | 16% | NO TRIP |  | ✓/✗
LV L3-Blue | 0.256 | 300° | 0.041 | 300° | 16% | NO TRIP |  | ✓/✗
B. 5th HARMONIC RESTRAINT TEST (Overexcitation – 250 Hz) ¦ Threshold = 40%
Phase | Fund. I (A) 50 Hz | Fund. Angle | Harm. I (A) 250 Hz | Harm. Angle | Ratio (%) | Expected | Actual | Pass/Fail
HV L1-Red | 0.055 | 0° | 0.0231 | 0° | 42% | NO TRIP |  | ✓/✗
HV L2-Yellow | 0.055 | -120° | 0.0231 | -120° | 42% | NO TRIP |  | ✓/✗
HV L3-Blue | 0.055 | 120° | 0.0231 | 120° | 42% | NO TRIP |  | ✓/✗
LV L1-Red | 0.068 | 180° | 0.0286 | 180° | 42% | NO TRIP |  | ✓/✗
LV L2-Yellow | 0.068 | 60° | 0.0286 | 60° | 42% | NO TRIP |  | ✓/✗
LV L3-Blue | 0.068 | 300° | 0.0286 | 300° | 42% | NO TRIP |  | ✓/✗
C. THRESHOLD VERIFICATION (above & below threshold – both states)
Harmonic | Threshold | Level ABOVE | Expected | Result | Level BELOW | Expected | Result | Pass/Fail
2nd Harmonic (Inrush) | 15% of Fund | HV: 0.0331A (16%) LV: 0.041A (16%) | NO TRIP |  | HV: 0.0248A (12%) LV: 0.031A (12%) | TRIP |  | ✓/✗
5th Harmonic (Overexcit.) | 40% of Fund | HV: 0.0231A (42%) LV: 0.0286A (42%) | NO TRIP |  | HV: 0.0193A (35%) LV: 0.0238A (35%) | TRIP |  | ✓/✗
ADD-ON STABILISATION (Addr. 1261A = 4.5×In): If I_bias > 4.5×In – extra stabilisation added for first half-cycle after fault inception to prevent false trip from CT saturation during heavy external faults. Calculated: I_t = 7404.8 A primary, I/In = 6.452×In → Set 4.5×In (from PDF addr. 1261A).
📋 NOTES, FORMULAS & STANDARDS — 87T HARMONIC RESTRAINT ¦ SET-2
📚 APPLICABLE STANDARDS
▪ IEC 60255-187-3 – Harmonic restraint requirements for transformer differential protection
▪ IEEE C37.91 – Guide for protecting power transformers
📐 KEY FORMULAS
LV harmonic test current (Set-2, 1600/1): I_fund_LV = 1.5 × I_NOb = 1.5 × 0.683 = 0.256 A
LV 2nd harm (Set-2): 0.256 × 0.16 = 0.041 A at 100 Hz (Set-1: 0.027 A at 100 Hz – different)
LV 5th harm (Set-2): 0.068 × 0.42 = 0.029 A at 250 Hz
2nd harm ratio = I_2nd/I_fund × 100 → > 15%: BLOCK ¦ < 15%: ALLOW TRIP
5th harm ratio = I_5th/I_fund × 100 → > 40%: BLOCK ¦ < 40%: ALLOW TRIP
Cross-block = 25 cycles × 20ms = 500 ms (same for Set-1 and Set-2)
Add-on stab: IDT = 7404.8A primary, I/In = 7404.8/1093.47 = 6.77×In → Set 4.5×In
📝 TESTING NOTES & GUIDANCE
• Set-2 LV harmonic test currents differ from Set-1 due to higher LV base current (0.683 vs 0.456A).
• HV harmonic test currents are identical between Set-1 and Set-2 (same HV CT ratio).
• Test set must support simultaneous dual-frequency injection.
• Cross-block (addr 1272 = 25 cycles) prevents false trip on single-phase fault during 3-phase inrush.
• Add-on stabilisation (4.5×In) verified via relay display during high current slope-2 tests.
• I-Diff >> = 10.0×In unrestrained: not blocked by harmonics (heavy fault always trips).
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## A.3-HV OC-EF
ABC GRID STATION – 250 MVA AUTO-TRANSFORMER T-1 ¦ RELAY TESTING PROTOCOL
A.3 HV (220 kV) Overcurrent & Earth Fault Protection
Relay Type: |  | Siemens 7SJ8021-5EB90-1FA0-LOS |  |  | System Voltage: |  | 220/132 kV
HV CT Ratio: |  | 1200/1A (Lower CT Core-3 & Mid CT Core-3) |  |  | LV CT Ratio: |  | N/A
HV Rated I: |  | I> = 1.2 A sec ¦ TMS = 0.14 ¦ NI curve |  |  | LV Rated I: |  | IE> = 0.19 A sec ¦ TMS = 0.32 ¦ NI curve
Sheet No: |  | 10 of 10 |  |  | Station:
A. RELAY SETTINGS SUMMARY (from Siemens Setting Calculation A.3)
Transformer HV Rating |  |  | 250 MVA, 220 kV ¦ HV Rated Current = 250,000/(√3×220) = 656.06 A primary
CT Ratio (HV) |  |  | 1200/1A – Lower CT Core-3 & Mid CT Core-3 (terminals 3S1-3S3)
OC Pickup (Phase) I> |  |  | 1.2 A secondary = 120% × In ¦ Primary: 1.2×1200 = 1440 A (addr 1221)
OC Curve Type |  |  | IEC Normal Inverse (NI) ¦ IEC 60255-151 (addr 1225)
OC TMS |  |  | 0.14 (addr 1224) ¦ Calculated operating time at fault level ≈ 0.902 sec
OC Instantaneous I>> |  |  | 3.5 A secondary = 4200 A primary (addr 1231)
EF Pickup (Neutral) IE> |  |  | 0.19 A secondary = 19% × In ¦ Primary: 0.19×1200 = 228 A (addr 1231A)
EF Curve Type |  |  | IEC Normal Inverse (NI) ¦ IEC 60255-151 (addr 1225)
EF TMS |  |  | 0.32 (addr 1224) ¦ Calculated operating time at fault level ≈ 0.746 sec
EF Instantaneous IE>> |  |  | 4.16 A secondary (addr 1231)
Max System Fault Current |  |  | 4214 A primary (= 250/(0.1557×√3×220)×1000)
OC Multiples of Pickup (M) |  |  | M = 4214/(1200×1.2) = 2.93 ¦ t = 0.14×0.14/(2.93^0.02-1) = 0.902 sec
EF Multiples of Pickup (M) |  |  | M = 4214/(1200×0.19) = 18.48 ¦ t = 0.14×0.32/(18.48^0.02-1) = 0.746 sec
B. TEST 1 – PHASE OVERCURRENT PICKUP TEST (ANSI 51) ¦ Set = 1.2 A secondary
METHOD: Inject single-phase current, ramp slowly from 0 A upward. Record pickup (LED + contact closes). Then reduce current – record drop-off (≈ 95% of pickup). Acceptance: ±5% of 1.2 A = 1.14–1.26 A.
Test Phase | Set Pickup (A) | Apply 102% (A) | Pickup Observed (A) | Drop-off (A) | Error (%) | Trip Time (ms) | Pass/Fail | Initials
Phase L1 (Red) | 1.2 | 1.224 |  |  |  |  | ✓/✗
Phase L2 (Yellow) | 1.2 | 1.224 |  |  |  |  | ✓/✗
Phase L3 (Blue) | 1.2 | 1.224 |  |  |  |  | ✓/✗
C. TEST 2 – EARTH FAULT PICKUP TEST (ANSI 51N) ¦ Set = 0.19 A secondary
METHOD: Inject current into earth fault (neutral/residual) CT terminal. Ramp slowly from 0. Acceptance: ±5% of 0.19 A = 0.181–0.200 A. Drop-off: ≈ 0.180 A (95%). Be careful – EF is sensitive.
Element | Set Pickup (A) | Apply 102% (A) | Pickup Observed (A) | Drop-off (A) | Error (%) | Trip Time (ms) | Pass/Fail | Initials
Earth Fault IE> (Neutral) | 0.19 | 0.194 |  |  |  |  | ✓/✗
D. TEST 3 – IDMT TIMING TEST – PHASE OVERCURRENT (ANSI 51) ¦ TMS=0.14 ¦ NI Curve
METHOD: STEP-inject current (apply suddenly). Timer starts with current, stops at trip contact. Formula: t = 0.14×TMS/(M^0.02-1) where M = I_inject/I_pickup. Tolerance: ±5% OR ±35ms (whichever greater).
Test Level | Primary (A) | Secondary (A) | M = I/I> | Calc. Time (sec) | Time-1 (ms) | Time-2 (ms) | Avg. (ms) | Pass/Fail
2× Pickup | 2880 | 2.4 | 2 | 1.404 |  |  |  | ✓/✗
5× Pickup | 7200 | 6 | 5 | 0.599 |  |  |  | ✓/✗
10× Pickup | 14400 | 12 | 10 | 0.416 |  |  |  | ✓/✗
At Fault Level | 4214 | 3.51 | 2.93 | 0.902 |  |  |  | ✓/✗
E. TEST 4 – IDMT TIMING TEST – EARTH FAULT (ANSI 51N) ¦ TMS=0.32 ¦ NI Curve
METHOD: STEP-inject into earth fault CT terminal. Formula: t = 0.14×TMS/(M^0.02-1) with TMS=0.32. Tolerance: ±5% of calculated time OR ±35ms (whichever greater).
Test Level | Primary (A) | Secondary (A) | M = I/IE> | Calc. Time (sec) | Time-1 (ms) | Time-2 (ms) | Avg. (ms) | Pass/Fail
2× EF Pickup | 456 | 0.38 | 2 | 3.209 |  |  |  | ✓/✗
5× EF Pickup | 1140 | 0.95 | 5 | 1.37 |  |  |  | ✓/✗
10× EF Pickup | 2280 | 1.9 | 10 | 0.951 |  |  |  | ✓/✗
At Fault Level | 4214 | 3.51 | 18.48 | 0.746 |  |  |  | ✓/✗
F. TEST 5 – INSTANTANEOUS ELEMENT TEST (I>> Phase OC & IE>> Earth Fault)
METHOD: Apply STEP current well ABOVE instantaneous setting. Relay must trip in < 50 ms. Then test at 95% of setting – relay must NOT trip instantaneously (security check).
Element | Set Value (A sec) | Test Level 110% (A) | Expected | Operated (Y/N) | Trip Time (ms) | Test 95% (A) | NOT Trip (Y/N) | Pass/Fail
I>> Phase OC | 3.5 A | 3.85 A | TRIP < 50 ms |  |  | 3.325 A | NOT TRIP | ✓/✗
IE>> Earth Fault | 4.16 A | 4.58 A | TRIP < 50 ms |  |  | 3.952 A | NOT TRIP | ✓/✗
G. OUTPUT CONTACT & INTEGRATION CHECKS
1 | Phase OC trip output contacts (T1–T2) energised on trip – verified at panel terminal | [6 empty] | ✓/✗
2 | Earth fault trip output contacts energised on EF trip signal | [6 empty] | ✓/✗
3 | Instantaneous elements (I>>, IE>>) trip contacts operate in < 50 ms | [6 empty] | ✓/✗
4 | TRIP LED and ALARM relay activate correctly on each function | [6 empty] | ✓/✗
5 | Event log records: fault type, injected current, operate time | [6 empty] | ✓/✗
6 | CB trip coil continuity confirmed via trip circuit (wiring to HV CB) | [6 empty] | ✓/✗
7 | Blocking input (BLOCK) verified to inhibit trip correctly when energised | [6 empty] | ✓/✗
8 | All relay settings confirmed unchanged after testing (read back from relay) | [6 empty] | ✓/✗
📋 NOTES, FORMULAS & STANDARDS — HV OC & EF PROTECTION ¦ A.3
📚 APPLICABLE STANDARDS
▪ IEC 60255-151 – Functional requirements for IDMT overcurrent and earth fault protection
▪ IEC 60255-26 – EMC requirements for measuring relays and protection equipment
▪ ANSI/IEEE C37.90 – Relay and relay systems associated with electric power apparatus
▪ BS 142 – Electrical protection relays
▪ NTDC/WAPDA HV Protection Relay Testing & Commissioning Guidelines
📐 KEY FORMULAS
HV rated current: I_rated = S/(√3×V) = 250,000/(√3×220) = 656.06 A primary
OC primary pickup = I>(sec) × CT = 1.2 × 1200 = 1440 A (≈ 2.2× rated)
EF primary pickup = IE>(sec) × CT = 0.19 × 1200 = 228 A (≈ 35% rated)
IEC Normal Inverse (NI): t = 0.14 × TMS / (M^0.02 − 1)
OC at fault: M = 4214/(1200×1.2) = 2.93 → t = 0.14×0.14/(2.93^0.02-1) = 0.902 sec
EF at fault: M = 4214/(1200×0.19) = 18.48 → t = 0.14×0.32/(18.48^0.02-1) = 0.746 sec
TMS calc: TMS = t_required / t_at_TMS=1 → OC: TMS = 1.0/6.442 = 0.155 → Selected 0.14
Max fault: I_fault = S/(√3×V×%Z) = 250,000/(√3×220×0.1557) = 4214 A primary
Error% = ¦Measured − Calculated¦ / Calculated × 100 → must be ≤ 5%
Tolerance: ±5% of calculated time OR ±35 ms (whichever is greater)
📝 TESTING NOTES & GUIDANCE
• Always use STEP injection (sudden application) for timing tests – NOT ramp injection.
• Pickup test: ramp slowly from 0 to find exact pickup. Ramped injection for pickup ONLY.
• OC pickup tolerance: ±5% → acceptable range: 1.14–1.26 A secondary.
• EF pickup tolerance: ±5% → acceptable range: 0.181–0.200 A secondary.
• Inject OC into phase CT terminals (3S1-3S3 for Lower Core). EF into neutral/residual CT.
• DO NOT confuse HV OC/EF CT terminals with Differential relay (87T) CT terminals.
• Instantaneous element (I>>) must trip in < 50 ms. Use ms-resolution timer.
• At 95% of I>>: relay must NOT trip instantaneously (may trip on IDMT after delay – OK).
• After all tests: read back all relay addresses to confirm settings unchanged.
• Record relay serial number and firmware version on cover sheet.
TESTING ACCEPTANCE SIGN-OFF
TESTED BY (Protection Engineer & Test Inspector) |  | CHECKED BY (Senior Engineer) |  | WITNESSED BY (Client/NTDC) |  | APPROVED BY (Project Manager)
Name: |  | Name: |  | Name: |  | Name:
Designation: |  | Designation: |  | Designation: |  | Designation:
Signature: |  | Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: |  | Date:

## Test Summary
ABC G/S – 250 MVA AUTO-TRANSFORMER T-1 ¦ TEST SUMMARY & DEFECTS LOG
Differential Set-1 (A.1) ¦ Differential Set-2 (A.2) ¦ HV OC & EF (A.3)
A. TEST SECTION SUMMARY
Sheet | Protection Function | No. Tests | Passed | Failed | Overall | Witnessed By
A.1-Pre-Test | Pre-Test Checks & Insulation Resistance (Set-1) |  |  |  | PENDING
A.1-Diff Pickup | 87T Differential Set-1 – Pickup, Drop-off & Stability |  |  |  | PENDING
A.1-Slope Test | 87T Differential Set-1 – Slope Characteristic (30% / 60%) |  |  |  | PENDING
A.1-Harmonic | 87T Differential Set-1 – Harmonic Restraint (2nd=15%, 5th=40%) |  |  |  | PENDING
A.1-Buchholz | Buchholz, OTI, WTI, PRV & Oil Level (ANSI 26/63) |  |  |  | PENDING
A.2-Pre-Test | Pre-Test Checks & Insulation Resistance (Set-2, LV CT=1600/1) |  |  |  | PENDING
A.2-Diff Pickup | 87T Differential Set-2 – Pickup, Drop-off & Stability |  |  |  | PENDING
A.2-Slope Test | 87T Differential Set-2 – Slope Characteristic (30% / 60%) |  |  |  | PENDING
A.2-Harmonic | 87T Differential Set-2 – Harmonic Restraint (2nd=15%, 5th=40%) |  |  |  | PENDING
A.3-HV OC-EF | HV (220kV) OC (51): I>=1.2A, TMS=0.14 ¦ EF (51N): IE>=0.19A, TMS=0.32 |  |  |  | PENDING
B. DEFECTS / NON-CONFORMANCES LOG
No. | Description of Defect / Non-Conformance | Sheet Ref | Raised By | Date | Status | Closed By
1
2
3
4
5
6
7
OVERALL RESULT: □ PASS □ FAIL □ CONDITIONAL PASS
General Comments / Conditions / Recommendations: